## Elec
Supply ID | Minisub | Kiosk | Stand / Supply | Supply Type | Breaker | Phase | Meter Serial | Occupancy | AMR Installed | AMR Device | AMR Port | AMR Label | AMR Last Comms | AMR Order | Source | Comments
ZLM-0001 | MS 01 | 505 Aura K01 | 505-01 | Stand | 63A | B | 84039740 | Occupied | FALSE | [5 empty] | MS 01!V16
ZLM-0002 | MS 01 | 505 Aura K01 | 505-02 | Stand | 63A | R | 75091206 | Occupied | FALSE | [5 empty] | MS 01!V17
ZLM-0003 | MS 01 | 505 Aura K01 | 505-03 | Stand | 63A | R | 84039751 | Occupied | FALSE | [5 empty] | MS 01!V18
ZLM-0004 | MS 01 | 505 Aura K01 | 505-04 | Stand | 63A | W | 84039746 | Occupied | FALSE | [5 empty] | MS 01!V19
ZLM-0005 | MS 01 | 505 Aura K02 | 505-05 | Stand | 63A | B | 75091343 | Occupied | FALSE | [5 empty] | MS 01!V24
ZLM-0006 | MS 01 | 505 Aura K02 | 505-06 | Stand | 63A | W | 75091296 | Occupied | FALSE | [5 empty] | MS 01!V25
ZLM-0007 | MS 01 | 505 Aura K02 | 505-07 | Stand | 63A | R | 84039707 | Occupied | FALSE | [5 empty] | MS 01!V26
ZLM-0008 | MS 01 | 505 Aura K02 | 505-08 | Stand | 63A | W | 62742631 | Occupied | FALSE | [5 empty] | MS 01!V27
ZLM-0009 | MS 01 | 505 Aura K03 | 505-09 | Stand | 63A | B | 47369314 | Occupied | FALSE | [5 empty] | MS 01!V32
ZLM-0010 | MS 01 | 505 Aura K03 | 505-10 | Stand | 63A | B | 47369294 | Occupied | FALSE | [5 empty] | MS 01!V33
ZLM-0011 | MS 01 | 505 Aura K03 | 505-11 | Stand | 63A | R | 75091021 | Occupied | FALSE | [5 empty] | MS 01!V34
ZLM-0012 | MS 01 | 505 Aura K03 | 505-12 | Stand | 63A | W | 75091242 | Occupied | FALSE | [5 empty] | MS 01!V35
ZLM-0013 | MS 01 | 505 Aura K08 | 505-F1 | Stand | 63A | B | 85354288 | Occupied | FALSE | [5 empty] | MS 01!Q41
ZLM-0014 | MS 01 | 505 Aura K08 | 505-F2 | Stand | 63A | R | 85354624 | Occupied | FALSE | [5 empty] | MS 01!Q42
ZLM-0015 | MS 01 | 505 Aura K08 | 505-F3 | Stand | 63A | W | 85354356 | Occupied | FALSE | [5 empty] | MS 01!Q43
ZLM-0016 | MS 01 | 505 Aura K08 | 505-F4 | Stand | 63A | W | 85354293 | Occupied | FALSE | [5 empty] | MS 01!Q44
ZLM-0017 | MS 01 | 505 Aura K08 | 505-F5 | Stand | 63A | R | 85354298 | Occupied | FALSE | [5 empty] | MS 01!Q45
ZLM-0018 | MS 01 | 505 Aura K08 | 505-45 | Stand | 63A | W | 85354586 | Occupied | FALSE | [5 empty] | MS 01!Q46
ZLM-0019 | MS 01 | 505 Aura K04 | 505-13 | Stand | 63A | B | 75091218 | Occupied | FALSE | [5 empty] | MS 01!V41
ZLM-0020 | MS 01 | 505 Aura K04 | 505-14 | Stand | 63A | R | 75091285 | Occupied | FALSE | [5 empty] | MS 01!V42
ZLM-0021 | MS 01 | 505 Aura K04 | 505-15 | Stand | 63A | R | 75091205 | Occupied | FALSE | [5 empty] | MS 01!V43
ZLM-0022 | MS 01 | 505 Aura K04 | 505-16 | Stand | 63A | W | 75091069 | Occupied | FALSE | [5 empty] | MS 01!V44
ZLM-0023 | MS 01 | 505 Aura K04 | Clubhouse | Common / other | 63A | R | 71205156 | Occupied | FALSE | [5 empty] | MS 01!V45
ZLM-0024 | MS 01 | 505 Aura K05 | 505-17 | Stand | 63A | B | 75091280 | Occupied | FALSE | [5 empty] | MS 01!V50
ZLM-0025 | MS 01 | 505 Aura K05 | 505-18 | Stand | 63A | W | 75091254 | Occupied | FALSE | [5 empty] | MS 01!V51
ZLM-0026 | MS 01 | 505 Aura K05 | 505-19 | Stand | 63A | R | 75091309 | Occupied | FALSE | [5 empty] | MS 01!V52
ZLM-0027 | MS 01 | 505 Aura K05 | 505-20 | Stand | 63A | W | 75091345 | Occupied | FALSE | [5 empty] | MS 01!V53
ZLM-0028 | MS 01 | 505 Aura K09 | 505-29 | Stand | 63A | B | 84340966 | Occupied | FALSE | [5 empty] | MS 01!Q51
ZLM-0029 | MS 01 | 505 Aura K09 | 505-30 | Stand | 63A | R | 84341038 | Occupied | FALSE | [5 empty] | MS 01!Q52
ZLM-0030 | MS 01 | 505 Aura K09 | 505-31 | Stand | 63A | B | 84341019 | Occupied | FALSE | [5 empty] | MS 01!Q53
ZLM-0031 | MS 01 | 505 Aura K09 | 505-32 | Stand | 63A | W | 84340990 | Occupied | FALSE | [5 empty] | MS 01!Q54
ZLM-0032 | MS 01 | 505 Aura K06 | 505-21 | Stand | 63A | B | 75091291 | Occupied | FALSE | [5 empty] | MS 01!V58
ZLM-0033 | MS 01 | 505 Aura K06 | 505-22 | Stand | 63A | W | 75091253 | Occupied | FALSE | [5 empty] | MS 01!V59
ZLM-0034 | MS 01 | 505 Aura K06 | 505-23 | Stand | 63A | B | 75091283 | Occupied | FALSE | [5 empty] | MS 01!V60
ZLM-0035 | MS 01 | 505 Aura K06 | 505-24 | Stand | 63A | R | 75091272 | Occupied | FALSE | [5 empty] | MS 01!V61
ZLM-0036 | MS 01 | 505 Aura K10 | 505-33 | Stand | 63A | R | 84340995 | Occupied | FALSE | [5 empty] | MS 01!Q59
ZLM-0037 | MS 01 | 505 Aura K10 | 505-34 | Stand | 63A | W | 84340900 | Occupied | FALSE | [5 empty] | MS 01!Q60
ZLM-0038 | MS 01 | 505 Aura K10 | 505-35 | Stand | 63A | B | 84340901 | Occupied | FALSE | [5 empty] | MS 01!Q61
ZLM-0039 | MS 01 | 505 Aura K10 | 505-36 | Stand | 63A | R | 84340949 | Occupied | FALSE | [5 empty] | MS 01!Q62
ZLM-0040 | MS 01 | 505 Aura K07 | 505-25 | Stand | 63A | B | 75091217 | Occupied | FALSE | [5 empty] | MS 01!V66
ZLM-0041 | MS 01 | 505 Aura K07 | 505-26 | Stand | 63A | R | 75091229 | Occupied | FALSE | [5 empty] | MS 01!V67
ZLM-0042 | MS 01 | 505 Aura K07 | 505-27 | Stand | 63A | R | 75091189 | Occupied | FALSE | [5 empty] | MS 01!V68
ZLM-0043 | MS 01 | 505 Aura K07 | 505-28 | Stand | 63A | W | 75091277 | Occupied | FALSE | [5 empty] | MS 01!V69
ZLM-0044 | MS 01 | 505 Aura K11 | 505-37 | Stand | 63A | R | 84340973 | Occupied | FALSE | [5 empty] | MS 01!Q67
ZLM-0045 | MS 01 | 505 Aura K11 | 505-38 | Stand | 63A | W | 84340996 | Occupied | FALSE | [5 empty] | MS 01!Q68
ZLM-0046 | MS 01 | 505 Aura K11 | 505-39 | Stand | 63A | B | 84340929 | Occupied | FALSE | [5 empty] | MS 01!Q69
ZLM-0047 | MS 01 | 505 Aura K11 | 505-40 | Stand | 63A | W | 84340924 | Occupied | FALSE | [5 empty] | MS 01!Q70
ZLM-0048 | MS 01 | 505 Aura K12 | 505-41 | Stand | 63A | R | 84340927 | Occupied | FALSE | [5 empty] | MS 01!Q75
ZLM-0049 | MS 01 | 505 Aura K12 | 505-42 | Stand | 63A | W | 84340905 | Occupied | FALSE | [5 empty] | MS 01!Q76
ZLM-0050 | MS 01 | 505 Aura K12 | 505-43 | Stand | 63A | B | 84340972 | Occupied | FALSE | [5 empty] | MS 01!Q77
ZLM-0051 | MS 01 | 505 Aura K12 | 505-44 | Stand | 63A | B | 84340948 | Occupied | FALSE | [5 empty] | MS 01!Q78
ZLM-0052 | MS 01 | MS LV board | Main Gatehouse | Common / other | 60A - Double Connection | RWB? |  | Occupied | FALSE | [5 empty] | MS 01!row 10
ZLM-0053 | MS 01 | MS LV board | Contractors Gate | Common / other | 60A - Double Connection | RWB? |  | Occupied | FALSE | [5 empty] | MS 01!row 10
ZLM-0054 | MS 01 | MS LV board | Streetlights | Common / other | 60A | RWB? | 82816209 | Occupied | FALSE | [5 empty] | MS 01!row 10
ZLM-0055 | MS 02 | K 2,1 | 510 | Stand | 63A | R | 63038508 | Occupied | FALSE | [5 empty] | MS 02!G16
ZLM-0056 | MS 02 | K 2,1 | 507 | Stand | 63A | W | 75091043 | Occupied | FALSE | [5 empty] | MS 02!G17
ZLM-0057 | MS 02 | K 2,1 | 508 | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 02!G18
ZLM-0058 | MS 02 | K 2,1 | 509 | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 02!G19
ZLM-0059 | MS 02 | K 2,1 | 1308 | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 02!G20
ZLM-0060 | MS 02 | K 2,1 | 1309 | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 02!G21
ZLM-0061 | MS 02 | 513 Azure LV Kiosk | S/L Kiosk | Common / other | 63A | RWB |  | Unknown | FALSE | [5 empty] | MS 02!Q18
ZLM-0062 | MS 02 | 512 Kiosk 1 | 512 - 01 | Stand | 63A | R | 91732536 | Occupied | FALSE | [5 empty] | MS 02!V16
ZLM-0063 | MS 02 | 512 Kiosk 1 | 512 - 02 | Stand | 63A | R | 91732507 | Occupied | FALSE | [5 empty] | MS 02!V17
ZLM-0064 | MS 02 | 512 Kiosk 1 | Builders | Common / other | 63A | W | 68053971 | Under construction | FALSE | [5 empty] | MS 02!V18
ZLM-0065 | MS 02 | 512 Kiosk 2 | 512 - 03 | Stand | 63A | R | 91732516 | Occupied | FALSE | [5 empty] | MS 02!V24
ZLM-0066 | MS 02 | 512 Kiosk 2 | - | Stand | 63A | W |  | Unknown | FALSE | [5 empty] | MS 02!V25 | Placeholder slot
ZLM-0067 | MS 02 | 512 Kiosk 2 | - | Stand | - | - |  | Unknown | FALSE | [5 empty] | MS 02!V26 | Placeholder slot
ZLM-0068 | MS 02 | 513 K 1,1 | 513 - 01 | Stand | 63A | W | 75091074 | Occupied | FALSE | [5 empty] | MS 02!Q26
ZLM-0069 | MS 02 | 513 K 1,1 | 513 - 09 | Stand | 63A | R | 90007816 | Occupied | FALSE | [5 empty] | MS 02!Q27
ZLM-0070 | MS 02 | 513 K 1,2 | 513 - 02 | Stand | 63A | R | 75091123 | Occupied | FALSE | [5 empty] | MS 02!Q32
ZLM-0071 | MS 02 | 513 K 1,2 | 513 - 03 | Stand | 63A | W | 75091105 | Occupied | FALSE | [5 empty] | MS 02!Q33
ZLM-0072 | MS 02 | 513 K 1,2 | 513 - 07 | Stand | 63A | B | 75091049 | Occupied | FALSE | [5 empty] | MS 02!Q34
ZLM-0073 | MS 02 | 513 K 1,2 | 513 - 08 | Stand | 63A | R | 75091098 | Occupied | FALSE | [5 empty] | MS 02!Q35
ZLM-0074 | MS 02 | 512 Kiosk 3 | - | Stand | - | - |  | Unknown | FALSE | [5 empty] | MS 02!V35 | Placeholder slot
ZLM-0075 | MS 02 | 512 Kiosk 3 | - | Stand | - | - |  | Unknown | FALSE | [5 empty] | MS 02!V36 | Placeholder slot
ZLM-0076 | MS 02 | 513 K 1,3 | 513 - 04 | Stand | 63A | R | 75091086 | Occupied | FALSE | [5 empty] | MS 02!Q40
ZLM-0077 | MS 02 | 513 K 1,3 | 513 - 05 | Stand | 63A | B | 75091068 | Occupied | FALSE | [5 empty] | MS 02!Q41
ZLM-0078 | MS 02 | 513 K 1,3 | 513 - 06 | Stand | 63A | B | 75091112 | Occupied | FALSE | [5 empty] | MS 02!Q42
ZLM-0079 | MS 02 | 512 Kiosk 4 | 512 - 04 | Stand | 63A | R | 91732590 | Occupied | FALSE | [5 empty] | MS 02!V41
ZLM-0080 | MS 02 | 512 Kiosk 4 | 512 - 05 | Stand | 63A | W | 91732524 | Occupied | FALSE | [5 empty] | MS 02!V42
ZLM-0081 | MS 02 | 512 Kiosk 4 | 512 - 06 | Stand | 63A | W | 91732555 | Occupied | FALSE | [5 empty] | MS 02!V43
ZLM-0082 | MS 02 | 513 K 1,4 | 513 - 10 | Stand | 63A | R | 75091321 | Occupied | FALSE | [5 empty] | MS 02!Q47
ZLM-0083 | MS 02 | 513 K 1,4 | 513 - 11 | Stand | 63A | W | 75091094 | Occupied | FALSE | [5 empty] | MS 02!Q48
ZLM-0084 | MS 02 | 513 K 1,4 | 513 - 12 | Stand | 63A | B | 75091303 | Occupied | FALSE | [5 empty] | MS 02!Q49
ZLM-0085 | MS 02 | 512 Kiosk 5 | 512 - 07 | Stand | 63A | R | 91732599 | Occupied | FALSE | [5 empty] | MS 02!V49
ZLM-0086 | MS 02 | 512 Kiosk 5 | 512 - 08 | Stand | 63A | W | 91732577 | Occupied | FALSE | [5 empty] | MS 02!V50
ZLM-0087 | MS 02 | 512 Kiosk 5 | - | Stand | - | - |  | Unknown | FALSE | [5 empty] | MS 02!V51 | Placeholder slot
ZLM-0088 | MS 02 | 513 K 1,5 | 513 - 13 | Stand | 63A | R | 75091304 | Occupied | FALSE | [5 empty] | MS 02!Q54
ZLM-0089 | MS 02 | 513 K 1,5 | 513 - 14 | Stand | 63A | W | 75091172 | Occupied | FALSE | [5 empty] | MS 02!Q55
ZLM-0090 | MS 02 | 513 K 1,5 | 513 - 15 | Stand | 63A | B | 75091160 | Occupied | FALSE | [5 empty] | MS 02!Q56
ZLM-0091 | MS 02 | 513 K 1,5 | 513 - 16 | Stand | 63A | W | 75091026 | Occupied | FALSE | [5 empty] | MS 02!Q57
ZLM-0092 | MS 02 | 512 Kiosk 6 | - | Stand | - | - |  | Unknown | FALSE | [5 empty] | MS 02!V59 | Placeholder slot
ZLM-0093 | MS 02 | 512 Kiosk 6 | - | Stand | - | - |  | Unknown | FALSE | [5 empty] | MS 02!V60 | Placeholder slot
ZLM-0094 | MS 02 | MS LV board | Streetlights | Common / other | 60A | RWB? | 67021415 | Occupied | FALSE | [5 empty] | MS 02!row 10
ZLM-0095 | MS 03 | K 3,1 | 1324 | Stand | 50A | B | 85353970 | Occupied | FALSE | [5 empty] | MS 03!G16
ZLM-0096 | MS 03 | K 3,1 | ??? | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 03!G17 | Placeholder slot
ZLM-0097 | MS 03 | K 3,1 | ??? | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 03!G18 | Placeholder slot
ZLM-0098 | MS 03 | K 3,1 | ??? | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 03!G19 | Placeholder slot
ZLM-0099 | MS 03 | K 2,1 | 1336/01 | Stand | 50A | R | 85354387 | Occupied | FALSE | [5 empty] | MS 03!L16
ZLM-0100 | MS 03 | K 2,1 | 1336/02 | Stand | 50A | B | 85354155 | Occupied | FALSE | [5 empty] | MS 03!L17
ZLM-0101 | MS 03 | K 2,1 | 1336/03 | Stand | 50A | W | 85354395 | Occupied | FALSE | [5 empty] | MS 03!L18
ZLM-0102 | MS 03 | K 2,1 | 1336/04 | Stand | 50A | B | 85354414 | Occupied | FALSE | [5 empty] | MS 03!L19
ZLM-0103 | MS 03 | K 2,1 | 1336 / Comm | Stand | 50A | R | 71205180 | Occupied | FALSE | [5 empty] | MS 03!L20
ZLM-0104 | MS 03 | K 3,2 | 1318 | Stand | 50A | W | 75091219 | Occupied | FALSE | [5 empty] | MS 03!Q16
ZLM-0105 | MS 03 | K 3,2 | 1319 | Stand | 63A | B | 84039919 | Occupied | FALSE | [5 empty] | MS 03!Q17
ZLM-0106 | MS 03 | K 3,2 | 1320 | Stand | 50 | W | 85354223 | Occupied | FALSE | [5 empty] | MS 03!Q18
ZLM-0107 | MS 03 | K 3,2 | 1317 | Stand | 63A | R | 91733262 | Under construction | FALSE | [5 empty] | MS 03!Q19
ZLM-0108 | MS 03 | K 3,4 | ??? | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 03!V16 | Placeholder slot
ZLM-0109 | MS 03 | K 3,4 | ??? | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 03!V17 | Placeholder slot
ZLM-0110 | MS 03 | K 3,4 | ??? | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 03!V18 | Placeholder slot
ZLM-0111 | MS 03 | K 3,4 | ??? | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 03!V19 | Placeholder slot
ZLM-0112 | MS 03 | K 2,3 | 1326 | Stand | 63A | R | 91732981 | Under construction | FALSE | [5 empty] | MS 03!AA16
ZLM-0113 | MS 03 | K 2,3 | ??? | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 03!AA17 | Placeholder slot
ZLM-0114 | MS 03 | K 2,3 | ??? | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 03!AA18 | Placeholder slot
ZLM-0115 | MS 03 | K 2,3 | ??? | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 03!AA19 | Placeholder slot
ZLM-0116 | MS 03 | 1707 LV | S/L Kiosk | Stand | 30A | ??? |  | Unknown | FALSE | [5 empty] | MS 03!AF18
ZLM-0117 | MS 03 | 1707 K 3,7 | 1707/B 01 | Stand | 50A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AK20
ZLM-0118 | MS 03 | 1707 K 3,7 | 1707/B 02 | Stand | 50A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AK21
ZLM-0119 | MS 03 | 1707 K 3,7 | 1707/B 03 | Stand | 50A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AK22
ZLM-0120 | MS 03 | 1707 K 3,7 | 1707/B 04 | Stand | 50A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AK23
ZLM-0121 | MS 03 | 1707 K 3,7 | 1707/B 05 | Stand | 50A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AK24
ZLM-0122 | MS 03 | 1707 K 3,7 | 1707/B 06 | Stand | 50A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AK25
ZLM-0123 | MS 03 | 1707 K 3,7 | 1707/B 07 | Stand | 50A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AK26
ZLM-0124 | MS 03 | 1707 K 3,7 | 1707/B 08 | Stand | 50A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AK27
ZLM-0125 | MS 03 | 1707 K 3,7 | 1707/B 09 | Stand | 50A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AK28
ZLM-0126 | MS 03 | 1707 K 3,7 | 1707/B 10 | Stand | 50A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AK29
ZLM-0127 | MS 03 | 1707 K 3,7 | 1707/B 11 | Stand | 50A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AK30
ZLM-0128 | MS 03 | 1707 K 3,7 | 1707/B 12 | Stand | 50A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AK31
ZLM-0129 | MS 03 | 1707 K 3,7 | Ex/Lights | Common / other | 30A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AK32
ZLM-0130 | MS 03 | 1707 K 3,7 | Ex/Lights | Common / other | 30A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AK33
ZLM-0131 | MS 03 | 1707 K 3,4 | 1707/D 07 | Stand | 50A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AP20
ZLM-0132 | MS 03 | 1707 K 3,4 | 1707/D 08 | Stand | 50A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AP21
ZLM-0133 | MS 03 | 1707 K 3,4 | 1707/D 09 | Stand | 50A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AP22
ZLM-0134 | MS 03 | 1707 K 3,4 | 1707/D 10 | Stand | 50A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AP23
ZLM-0135 | MS 03 | 1707 K 3,4 | 1707/D 11 | Stand | 50A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AP24
ZLM-0136 | MS 03 | 1707 K 3,4 | 1707/D 12 | Stand | 50A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AP25
ZLM-0137 | MS 03 | 1707 K 3,4 | S/Lights | Common / other | 30A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AP26
ZLM-0138 | MS 03 | K 3,3 | 1311 | Stand | 50A | - |  | Vacant | FALSE | [5 empty] | MS 03!Q24
ZLM-0139 | MS 03 | K 3,3 | 1312 | Stand | 50A | R | 47369896 | Occupied | FALSE | [5 empty] | MS 03!Q25
ZLM-0140 | MS 03 | K 3,3 | 1313 | Stand | 50A | B | 91546461 | Occupied | FALSE | [5 empty] | MS 03!Q26
ZLM-0141 | MS 03 | K 3,3 | 1314 | Stand | 50A | W | 84340682 | Occupied | FALSE | [5 empty] | MS 03!Q27
ZLM-0142 | MS 03 | K 3,3 | 1316 | Stand | 63A | B | 91732655 | Occupied | FALSE | [5 empty] | MS 03!Q28
ZLM-0143 | MS 03 | K 3,3 | 1315 | Stand | 63A | R | 91733420 | Occupied | FALSE | [5 empty] | MS 03!Q29
ZLM-0144 | MS 03 | K 3,5 | 1707_ DEV | Stand | 50A | R | 87778330 | Under construction | FALSE | [5 empty] | MS 03!V24
ZLM-0145 | MS 03 | K 3,5 | 1315 | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 03!V25
ZLM-0146 | MS 03 | K 3,5 | ??? | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 03!V26 | Placeholder slot
ZLM-0147 | MS 03 | K 3,5 | ??? | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 03!V27 | Placeholder slot
ZLM-0148 | MS 03 | K 2,4 | ??? | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 03!AA24 | Placeholder slot
ZLM-0149 | MS 03 | K 2,4 | ??? | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 03!AA25 | Placeholder slot
ZLM-0150 | MS 03 | K 2,4 | ??? | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 03!AA26 | Placeholder slot
ZLM-0151 | MS 03 | K 2,4 | ??? | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 03!AA27 | Placeholder slot
ZLM-0152 | MS 03 | 1707 K 3,10 | CP/Lights | Common / other | 30A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AF24
ZLM-0153 | MS 03 | 1707 K 3,10 | CP/Lights | Common / other | 30A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AF25
ZLM-0154 | MS 03 | 1707 K 3,10 | Garage DB | Common / other | 40A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AF26
ZLM-0155 | MS 03 | K 2,2 | 1336/05 | Stand | 50A | R | 85354410 | Occupied | FALSE | [5 empty] | MS 03!L25
ZLM-0156 | MS 03 | K 2,2 | 1336/06 | Stand | 50A | B | 85354419 | Occupied | FALSE | [5 empty] | MS 03!L26
ZLM-0157 | MS 03 | K 2,2 | 1336/07 | Stand | 50A | W | 85353989 | Occupied | FALSE | [5 empty] | MS 03!L27
ZLM-0158 | MS 03 | K 2,2 | 1336/08 | Stand | 50A | W | 85353961 | Occupied | FALSE | [5 empty] | MS 03!L28
ZLM-0159 | MS 03 | 1707 K 3,5 | 1707/D 01 | Stand | 50A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AP31
ZLM-0160 | MS 03 | 1707 K 3,5 | 1707/D 02 | Stand | 50A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AP32
ZLM-0161 | MS 03 | 1707 K 3,5 | 1707/D 03 | Stand | 50A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AP33
ZLM-0162 | MS 03 | 1707 K 3,5 | 1707/D 04 | Stand | 50A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AP34
ZLM-0163 | MS 03 | 1707 K 3,5 | 1707/D 05 | Stand | 50A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AP35
ZLM-0164 | MS 03 | 1707 K 3,5 | 1707/D 06 | Stand | 50A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AP36
ZLM-0165 | MS 03 | 1707 K 3,5 | S/Lights | Common / other | 30A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AP37
ZLM-0166 | MS 03 | K 3,10 | ??? | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 03!V32 | Placeholder slot
ZLM-0167 | MS 03 | K 3,10 | ??? | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 03!V33 | Placeholder slot
ZLM-0168 | MS 03 | K 3,10 | ??? | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 03!V34 | Placeholder slot
ZLM-0169 | MS 03 | K 3,10 | ??? | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 03!V35 | Placeholder slot
ZLM-0170 | MS 03 | 1707 K 3,8 | 1707/B 13 | Stand | 50A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AK38
ZLM-0171 | MS 03 | 1707 K 3,8 | 1707/B 14 | Stand | 50A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AK39
ZLM-0172 | MS 03 | 1707 K 3,8 | 1707/B 15 | Stand | 50A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AK40
ZLM-0173 | MS 03 | 1707 K 3,8 | 1707/B 16 | Stand | 50A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AK41
ZLM-0174 | MS 03 | 1707 K 3,8 | 1707/B 17 | Stand | 50A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AK42
ZLM-0175 | MS 03 | 1707 K 3,8 | 1707/B 18 | Stand | 50A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AK43
ZLM-0176 | MS 03 | 1707 K 3,8 | 1707/B 19 | Stand | 50A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AK44
ZLM-0177 | MS 03 | 1707 K 3,8 | 1707/B 20 | Stand | 50A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AK45
ZLM-0178 | MS 03 | 1707 K 3,8 | Ex/Lights | Common / other | 30A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AK46
ZLM-0179 | MS 03 | 1707 K 3,8 | Ex/Lights | Common / other | 30A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AK47
ZLM-0180 | MS 03 | 1707 K 3,6 | 1707/A 01 | Stand | 50A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AP42
ZLM-0181 | MS 03 | 1707 K 3,6 | 1707/A 02 | Stand | 50A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AP43
ZLM-0182 | MS 03 | 1707 K 3,6 | 1707/A 03 | Stand | 50A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AP44
ZLM-0183 | MS 03 | 1707 K 3,6 | 1707/A 04 | Stand | 50A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AP45
ZLM-0184 | MS 03 | 1707 K 3,6 | 1707/A 05 | Stand | 50A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AP46
ZLM-0185 | MS 03 | 1707 K 3,6 | 1707/A 06 | Stand | 50A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AP47
ZLM-0186 | MS 03 | 1707 K 3,6 | 1707/A 07 | Stand | 50A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AP48
ZLM-0187 | MS 03 | 1707 K 3,6 | 1707/A 08 | Stand | 50A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AP49
ZLM-0188 | MS 03 | 1707 K 3,6 | CP/Lights | Common / other | 30A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AP50
ZLM-0189 | MS 03 | 1707 K 3,6 | CP/Lights | Common / other | 30A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AP51
ZLM-0190 | MS 03 | 1707 K 3,9 | 1707/A 09 | Stand | 50A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AK52
ZLM-0191 | MS 03 | 1707 K 3,9 | 1707/A 10 | Stand | 50A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AK53
ZLM-0192 | MS 03 | 1707 K 3,9 | 1707/A 11 | Stand | 50A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AK54
ZLM-0193 | MS 03 | 1707 K 3,9 | 1707/A 12 | Stand | 50A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AK55
ZLM-0194 | MS 03 | 1707 K 3,9 | 1707/A 13 | Stand | 50A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AK56
ZLM-0195 | MS 03 | 1707 K 3,9 | 1707/A 14 | Stand | 50A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AK57
ZLM-0196 | MS 03 | 1707 K 3,9 | 1707/A 15 | Stand | 50A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AK58
ZLM-0197 | MS 03 | 1707 K 3,9 | 1707/A 16 | Stand | 50A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AK59
ZLM-0198 | MS 03 | 1707 K 3,9 | CP/Lights | Common / other | 30A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AK60
ZLM-0199 | MS 03 | 1707 K 3,9 | CP/Lights | Common / other | 30A | ??? |  | Vacant | FALSE | [5 empty] | MS 03!AK61
ZLM-0200 | MS 03 | MS LV board | Streetlights Kiosk | Common / other | 32A | RWB? | 82816206 | Occupied | FALSE | [5 empty] | MS 03!row 10
ZLM-0201 | MS 04 | K 1,1 | 163 | Stand | 63A | W | 91546324 | Occupied | FALSE | [5 empty] | MS 04 - Coral!B16
ZLM-0202 | MS 04 | K 1,1 | 189 | Stand | 63A | R | 91732889 | Occupied | FALSE | [5 empty] | MS 04 - Coral!B17
ZLM-0203 | MS 04 | K 1,1 | 198 | Stand | 63A | W | 91546177 | Occupied | FALSE | [5 empty] | MS 04 - Coral!B18
ZLM-0204 | MS 04 | K 1,1 | 199 | Stand | 63A | R | 91546182 | Occupied | FALSE | [5 empty] | MS 04 - Coral!B19
ZLM-0205 | MS 04 | K 1,1 | 200 | Stand | 63A | B | 91546274 | Occupied | FALSE | [5 empty] | MS 04 - Coral!B20
ZLM-0206 | MS 04 | K 1,4 | 185 | Stand | 63A | - | 91546232 | Occupied | FALSE | [5 empty] | MS 04 - Coral!G16
ZLM-0207 | MS 04 | K 1,4 | 186 | Stand | 63A | B | 91732851 | Occupied | FALSE | [5 empty] | MS 04 - Coral!G17
ZLM-0208 | MS 04 | K 1,4 | 187 | Stand | 63A | B | 91732898 | Occupied | FALSE | [5 empty] | MS 04 - Coral!G18
ZLM-0209 | MS 04 | K 1,4 | 188 | Stand | 63A | W | 91732859 | Occupied | FALSE | [5 empty] | MS 04 - Coral!G19
ZLM-0210 | MS 04 | K 1,4 | 190 | Stand | 63A | B | 91732938 | Occupied | FALSE | [5 empty] | MS 04 - Coral!G20
ZLM-0211 | MS 04 | K 1,4 | 191 | Stand | 63A | R | 91732887 | Occupied | FALSE | [5 empty] | MS 04 - Coral!G21
ZLM-0212 | MS 04 | K 1,4 | 192 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 04 - Coral!G22
ZLM-0213 | MS 04 | K 1,4 | 193 | Stand | 63A | W | 91546242 | Occupied | FALSE | [5 empty] | MS 04 - Coral!G23
ZLM-0214 | MS 04 | K 1,10 | 156 | Stand | 63A | W | 91546201 | Occupied | FALSE | [5 empty] | MS 04 - Coral!L16
ZLM-0215 | MS 04 | K 1,10 | 157 | Stand | 63A | B | 91546280 | Occupied | FALSE | [5 empty] | MS 04 - Coral!L17
ZLM-0216 | MS 04 | K 1,10 | 158 | Stand | 63A | R | 91546202 | Occupied | FALSE | [5 empty] | MS 04 - Coral!L18
ZLM-0217 | MS 04 | K 1,10 | 159 | Stand | 63A | B | 91546175 | Occupied | FALSE | [5 empty] | MS 04 - Coral!L19
ZLM-0218 | MS 04 | K 1,10 | 160 | Stand | 63A | B | 91546250 | Occupied | FALSE | [5 empty] | MS 04 - Coral!L20
ZLM-0219 | MS 04 | K 1,10 | 161 | Stand | 63A | W | 91546199 | Occupied | FALSE | [5 empty] | MS 04 - Coral!L21
ZLM-0220 | MS 04 | K 1,10 | 162 | Stand | 63A | R | 91546256 | Occupied | FALSE | [5 empty] | MS 04 - Coral!L22
ZLM-0221 | MS 04 | K 1,2 | 164 | Stand | 63A | R | 91546315 | Occupied | FALSE | [5 empty] | MS 04 - Coral!B25
ZLM-0222 | MS 04 | K 1,2 | 165 | Stand | 63A | W | 91546244 | Occupied | FALSE | [5 empty] | MS 04 - Coral!B26
ZLM-0223 | MS 04 | K 1,2 | 166 | Stand | 63A | W | 91546281 | Occupied | FALSE | [5 empty] | MS 04 - Coral!B27
ZLM-0224 | MS 04 | K 1,2 | 167 | Stand | 63A | R | 91546185 | Occupied | FALSE | [5 empty] | MS 04 - Coral!B28
ZLM-0225 | MS 04 | K 1,2 | 168 | Stand | 63A | B | 91546475 | Occupied | FALSE | [5 empty] | MS 04 - Coral!B29
ZLM-0226 | MS 04 | K 1,2 | Streetlights | Common / other | 25A | R |  | Occupied | FALSE | [5 empty] | MS 04 - Coral!B30
ZLM-0227 | MS 04 | K 1,11 | 137 | Stand | 63A | - | 91732985 | Occupied | FALSE | [5 empty] | MS 04 - Coral!L27
ZLM-0228 | MS 04 | K 1,11 | 138 | Stand | 63A | ?? | 91733227 | Occupied | FALSE | [5 empty] | MS 04 - Coral!L28
ZLM-0229 | MS 04 | K 1,11 | 139 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 04 - Coral!L29
ZLM-0230 | MS 04 | K 1,11 | 148 | Stand | 63A |  |  | Under construction | FALSE | [5 empty] | MS 04 - Coral!L30
ZLM-0231 | MS 04 | K 1,11 | 149 | Stand | 63A |  |  | Under construction | FALSE | [5 empty] | MS 04 - Coral!L31
ZLM-0232 | MS 04 | K 1,11 | 150 | Stand | 63A |  |  | Under construction | FALSE | [5 empty] | MS 04 - Coral!L32
ZLM-0233 | MS 04 | K 1,11 | 151 | Stand | 63A | R | 91546224 | Occupied | FALSE | [5 empty] | MS 04 - Coral!L33
ZLM-0234 | MS 04 | K 1,11 | 152 | Stand | 63A |  |  | Under construction | FALSE | [5 empty] | MS 04 - Coral!L34
ZLM-0235 | MS 04 | K 1,11 | Streetlights | Common / other | 25A | R |  | Occupied | FALSE | [5 empty] | MS 04 - Coral!L35
ZLM-0236 | MS 04 | K 1,6 | 179 | Stand | 63A | W | 91546193 | Occupied | FALSE | [5 empty] | MS 04 - Coral!G28
ZLM-0237 | MS 04 | K 1,6 | 180 | Stand | 63A | B | 91733074 | Occupied | FALSE | [5 empty] | MS 04 - Coral!G29
ZLM-0238 | MS 04 | K 1,6 | 184 | Stand | 63A | R | 91546191 | Occupied | FALSE | [5 empty] | MS 04 - Coral!G30
ZLM-0239 | MS 04 | K 1,6 | 194 | Stand | 63A | R | 91546247 | Occupied | FALSE | [5 empty] | MS 04 - Coral!G31
ZLM-0240 | MS 04 | K 1,6 | 195 | Stand | 63A | B | 91546245 | Occupied | FALSE | [5 empty] | MS 04 - Coral!G32
ZLM-0241 | MS 04 | K 1,6 | 196 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 04 - Coral!G33
ZLM-0242 | MS 04 | K 1,6 | 197 | Stand | 63A | W | 91546320 | Occupied | FALSE | [5 empty] | MS 04 - Coral!G34
ZLM-0243 | MS 04 | K 1,6 | 201 | Stand | 63A | R | 91546259 | Occupied | FALSE | [5 empty] | MS 04 - Coral!G35
ZLM-0244 | MS 04 | K 1,6 | Streetlights | Common / other | 25A | R |  | Occupied | FALSE | [5 empty] | MS 04 - Coral!G36
ZLM-0245 | MS 04 | K 1,3 | 169 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 04 - Coral!B35
ZLM-0246 | MS 04 | K 1,3 | 170 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 04 - Coral!B36
ZLM-0247 | MS 04 | K 1,3 | 171 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 04 - Coral!B37
ZLM-0248 | MS 04 | K 1,3 | 172 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 04 - Coral!B38
ZLM-0249 | MS 04 | K 1,3 | 173 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 04 - Coral!B39
ZLM-0250 | MS 04 | K 1,3 | 174 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 04 - Coral!B40
ZLM-0251 | MS 04 | K 1,7 | 175 | Stand | 63A | W | 91546290 | Occupied | FALSE | [5 empty] | MS 04 - Coral!G41
ZLM-0252 | MS 04 | K 1,7 | 176 | Stand | 63A | B | 91546269 | Occupied | FALSE | [5 empty] | MS 04 - Coral!G42
ZLM-0253 | MS 04 | K 1,7 | 177 | Stand | 63A | W | 91546273 | Occupied | FALSE | [5 empty] | MS 04 - Coral!G43
ZLM-0254 | MS 04 | K 1,7 | 178 | Stand | 63A | R | 91546265 | Occupied | FALSE | [5 empty] | MS 04 - Coral!G44
ZLM-0255 | MS 04 | K 1,7 | 181 | Stand | 63A | W | 91546272 | Occupied | FALSE | [5 empty] | MS 04 - Coral!G45
ZLM-0256 | MS 04 | K 1,7 | Pump Kiosk | Common / other | 32A | RWB |  | Occupied | FALSE | [5 empty] | MS 04 - Coral!G46
ZLM-0257 | MS 04 | K 1,15 | 135 | Stand | 63A | ?? | 91733032 | Occupied | FALSE | [5 empty] | MS 04 - Coral!L41
ZLM-0258 | MS 04 | K 1,15 | 136 | Stand | 63A | ?? | 91733045 | Occupied | FALSE | [5 empty] | MS 04 - Coral!L42
ZLM-0259 | MS 04 | K 1,15 | 154 | Stand | 63A | W | 91546174 | Occupied | FALSE | [5 empty] | MS 04 - Coral!L43
ZLM-0260 | MS 04 | K 1,15 | 155 | Stand | 63A | R | 91546231 | Occupied | FALSE | [5 empty] | MS 04 - Coral!L44
ZLM-0261 | MS 04 | K 1,15 | Borehole | Common / other | 20A | RWB |  | Occupied | FALSE | [5 empty] | MS 04 - Coral!L45
ZLM-0262 | MS 04 | K 1,12 | 130 | Stand | 63A |  |  | Under construction | FALSE | [5 empty] | MS 04 - Coral!Q41
ZLM-0263 | MS 04 | K 1,12 | 133 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 04 - Coral!Q42
ZLM-0264 | MS 04 | K 1,12 | 134 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 04 - Coral!Q43
ZLM-0265 | MS 04 | K 1,12 | 147 | Stand | 63A | R | 91546225 | Occupied | FALSE | [5 empty] | MS 04 - Coral!Q44
ZLM-0266 | MS 04 | K 1,8 | 202 | Stand | 63A | R | 91732870 | Occupied | FALSE | [5 empty] | MS 04 - Coral!B45
ZLM-0267 | MS 04 | K 1,8 | 203 | Stand | 63A | W | 91732883 | Occupied | FALSE | [5 empty] | MS 04 - Coral!B46
ZLM-0268 | MS 04 | K 1,8 | 204 | Stand | 63A | B | 91732885 | Occupied | FALSE | [5 empty] | MS 04 - Coral!B47
ZLM-0269 | MS 04 | K 1,8 | 205 | Stand | 63A | R | 91732909 | Occupied | FALSE | [5 empty] | MS 04 - Coral!B48
ZLM-0270 | MS 04 | K 1,13 | 121 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 04 - Coral!Q49
ZLM-0271 | MS 04 | K 1,13 | 122 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 04 - Coral!Q50
ZLM-0272 | MS 04 | K 1,13 | 125 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 04 - Coral!Q51
ZLM-0273 | MS 04 | K 1,13 | 126 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 04 - Coral!Q52
ZLM-0274 | MS 04 | K 1,13 | 129 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 04 - Coral!Q53
ZLM-0275 | MS 04 | K 1,13 | 143 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 04 - Coral!Q54
ZLM-0276 | MS 04 | K 1,13 | 144 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 04 - Coral!Q55
ZLM-0277 | MS 04 | K 1,13 | 145 | Stand | 63A | W | 91546249 | Occupied | FALSE | [5 empty] | MS 04 - Coral!Q56
ZLM-0278 | MS 04 | K 1,13 | 146 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 04 - Coral!Q57
ZLM-0279 | MS 04 | K 1,16 | 123 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 04 - Coral!L50
ZLM-0280 | MS 04 | K 1,16 | 124 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 04 - Coral!L51
ZLM-0281 | MS 04 | K 1,16 | 127 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 04 - Coral!L52
ZLM-0282 | MS 04 | K 1,16 | 128 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 04 - Coral!L53
ZLM-0283 | MS 04 | K 1,16 | 131 | Stand | 63A | B | 91733050 | Occupied | FALSE | [5 empty] | MS 04 - Coral!L54
ZLM-0284 | MS 04 | K 1,16 | 132 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 04 - Coral!L55
ZLM-0285 | MS 04 | K 1,9 | 1 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 04 - Coral!B53
ZLM-0286 | MS 04 | K 1,9 | 2 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 04 - Coral!B54
ZLM-0287 | MS 04 | K 1,9 | 3 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 04 - Coral!B55
ZLM-0288 | MS 04 | K 1,9 | 4 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 04 - Coral!B56
ZLM-0289 | MS 04 | K 1,9 | Streetlights | Common / other | 25A | W |  | Occupied | FALSE | [5 empty] | MS 04 - Coral!B57
ZLM-0290 | MS 04 | K 1,17 | 111 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 04 - Coral!L60
ZLM-0291 | MS 04 | K 1,17 | 112 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 04 - Coral!L61
ZLM-0292 | MS 04 | K 1,17 | 115 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 04 - Coral!L62
ZLM-0293 | MS 04 | K 1,17 | 116 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 04 - Coral!L63
ZLM-0294 | MS 04 | K 1,17 | 119 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 04 - Coral!L64
ZLM-0295 | MS 04 | K 1,17 | 120 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 04 - Coral!L65
ZLM-0296 | MS 04 | K G/H | Gatehouse | Common / other | 40A | R | 91732532 | Occupied | FALSE | [5 empty] | MS 04 - Coral!B62
ZLM-0297 | MS 04 | K 1,14 | 113 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 04 - Coral!Q62
ZLM-0298 | MS 04 | K 1,14 | 114 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 04 - Coral!Q63
ZLM-0299 | MS 04 | K 1,14 | 117 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 04 - Coral!Q64
ZLM-0300 | MS 04 | K 1,14 | 118 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 04 - Coral!Q65
ZLM-0301 | MS 04 | K 1,14 | 140 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 04 - Coral!Q66
ZLM-0302 | MS 04 | K 1,14 | 141 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 04 - Coral!Q67
ZLM-0303 | MS 04 | K 1,14 | 142 | Stand | 63A | R | 91732910 | Occupied | FALSE | [5 empty] | MS 04 - Coral!Q68
ZLM-0304 | MS 05 | K 2,5 | 1 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!G16
ZLM-0305 | MS 05 | K 2,5 | 8 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!G17
ZLM-0306 | MS 05 | K 2,5 | 35 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!G18
ZLM-0307 | MS 05 | K 2,5 | 36 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!G19
ZLM-0308 | MS 05 | K 2,5 | 37 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!G20
ZLM-0309 | MS 05 | K 2,5 | Streetlights | Common / other | 10A | RWB |  | Occupied | FALSE | [5 empty] | MS 05 - Coral!G21
ZLM-0310 | MS 05 | K 2,5 | Unit (??) | Stand | 63A | - |  | Occupied | FALSE | [5 empty] | MS 05 - Coral!G22 | Placeholder slot
ZLM-0311 | MS 05 | K 2,5 | Unit (??) | Stand | 63A | - |  | Occupied | FALSE | [5 empty] | MS 05 - Coral!G23 | Placeholder slot
ZLM-0312 | MS 05 | K 2,5 | Plant Room | Common / other | 60A | RWB |  | Occupied | FALSE | [5 empty] | MS 05 - Coral!G24
ZLM-0313 | MS 05 | K 2,9 | 38 | Stand | 63A | ?? | 91732547 | Occupied | FALSE | [5 empty] | MS 05 - Coral!L16
ZLM-0314 | MS 05 | K 2,9 | 39 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!L17
ZLM-0315 | MS 05 | K 2,9 | 40 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!L18
ZLM-0316 | MS 05 | K 2,9 | 88 | Stand | 63A | ?? | 91732521 | Occupied | FALSE | [5 empty] | MS 05 - Coral!L19
ZLM-0317 | MS 05 | K 2,9 | 89 | Stand | 63A | ?? | 91732584 | Occupied | FALSE | [5 empty] | MS 05 - Coral!L20
ZLM-0318 | MS 05 | K 2,9 | 90 | Stand | 63A | - | 91732583 | Occupied | FALSE | [5 empty] | MS 05 - Coral!L21
ZLM-0319 | MS 05 | K 2,10 | 41 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!Q16
ZLM-0320 | MS 05 | K 2,10 | 42 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!Q17
ZLM-0321 | MS 05 | K 2,10 | 43 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!Q18
ZLM-0322 | MS 05 | K 2,10 | 44A | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!Q19
ZLM-0323 | MS 05 | K 2,10 | 64 | Stand | 63A | ?? | 91732512 | Occupied | FALSE | [5 empty] | MS 05 - Coral!Q20
ZLM-0324 | MS 05 | K 2,10 | 65 | Stand | 63A | ?? | 91732567 | Occupied | FALSE | [5 empty] | MS 05 - Coral!Q21
ZLM-0325 | MS 05 | K 2,10 | 66 | Stand | 63A | ?? | 91732585 | Occupied | FALSE | [5 empty] | MS 05 - Coral!Q22
ZLM-0326 | MS 05 | K 2,21 | Care Centre | Common / other | 320A | RWB | 93005964 | Occupied | FALSE | [5 empty] | MS 05 - Coral!AF20
ZLM-0327 | MS 05 | K 2,21 | Utilities | Common / other | 63A | RWB | 94991686 | Occupied | FALSE | [5 empty] | MS 05 - Coral!AF21
ZLM-0328 | MS 05 | K 2,21 | Streetlights | Common / other | 10A | RWB |  | Occupied | FALSE | [5 empty] | MS 05 - Coral!AF22
ZLM-0329 | MS 05 | K 2,3 – Block B | DB-B-01 | Common / other | 150A | 70mm |  | Unknown | FALSE | [5 empty] | MS 05 - Coral!V22
ZLM-0330 | MS 05 | K 2,3 – Block B | Plant Room | Common / other | 63A | 25mm |  | Unknown | FALSE | [5 empty] | MS 05 - Coral!V23
ZLM-0331 | MS 05 | K 2,14 | 91 | Stand | 63A | ?? | 91732665 | Occupied | FALSE | [5 empty] | MS 05 - Coral!L26
ZLM-0332 | MS 05 | K 2,14 | 92 | Stand | 63A | ?? | 91732605 | Occupied | FALSE | [5 empty] | MS 05 - Coral!L27
ZLM-0333 | MS 05 | K 2,14 | 93 | Stand | 63A | ?? | 91732666 | Occupied | FALSE | [5 empty] | MS 05 - Coral!L28
ZLM-0334 | MS 05 | K 2,2 | Wellness Cen | Common / other | 63A | RWB | 67021439 | Occupied | FALSE | [5 empty] | MS 05 - Coral!AF28
ZLM-0335 | MS 05 | K 2,2 | Streetlights | Common / other | 10A | RWB |  | Occupied | FALSE | [5 empty] | MS 05 - Coral!AF29
ZLM-0336 | MS 05 | K 2,2 | Care Centre | Common / other | 250A | RWB |  | Occupied | FALSE | [5 empty] | MS 05 - Coral!AF30
ZLM-0337 | MS 05 | K 2,2 | Plant Room | Common / other | 63A | RWB |  | Occupied | FALSE | [5 empty] | MS 05 - Coral!AF31
ZLM-0338 | MS 05 | K 2,6 | 9 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!G29
ZLM-0339 | MS 05 | K 2,6 | 10 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!G30
ZLM-0340 | MS 05 | K 2,6 | 11 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!G31
ZLM-0341 | MS 05 | K 2,6 | 12 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!G32
ZLM-0342 | MS 05 | K 2,6 | 31 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!G33
ZLM-0343 | MS 05 | K 2,6 | 33 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!G34
ZLM-0344 | MS 05 | K 2,6 | 34 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!G35
ZLM-0345 | MS 05 | K 2,11A | 67 | Stand | 63A | ?? | 91732548 | Occupied | FALSE | [5 empty] | MS 05 - Coral!Q29
ZLM-0346 | MS 05 | K 2,11A | 68 | Stand | 63A | ?? | 91732556 | Occupied | FALSE | [5 empty] | MS 05 - Coral!Q30
ZLM-0347 | MS 05 | K 2,11A | 69 | Stand | 63A | ?? | 91732572 | Occupied | FALSE | [5 empty] | MS 05 - Coral!Q31
ZLM-0348 | MS 05 | K 2,11A | 70 | Stand | 63A | ?? | 91732568 | Occupied | FALSE | [5 empty] | MS 05 - Coral!Q32
ZLM-0349 | MS 05 | K 2,11A | 71 | Stand | 63A | ?? | 91732626 | Occupied | FALSE | [5 empty] | MS 05 - Coral!Q33
ZLM-0350 | MS 05 | K 2,11A | 72 | Stand | 63A | ?? | 91732622 | Occupied | FALSE | [5 empty] | MS 05 - Coral!Q34
ZLM-0351 | MS 05 | K 2,11A | Streetlights | Common / other | 10A | RWB |  | Occupied | FALSE | [5 empty] | MS 05 - Coral!Q35
ZLM-0352 | MS 05 | K 2,4 – Block A | DB-A-01 | Common / other | 80A | Cable Size |  | Unknown | FALSE | [5 empty] | MS 05 - Coral!V29
ZLM-0353 | MS 05 | K 2,15 | 94 | Stand | 63A | ?? | 91732613 | Occupied | FALSE | [5 empty] | MS 05 - Coral!L33
ZLM-0354 | MS 05 | K 2,15 | 95 | Stand | 63A | ?? | 91732603 | Occupied | FALSE | [5 empty] | MS 05 - Coral!L34
ZLM-0355 | MS 05 | K 2,15 | 96 | Stand | 63A | ?? | 91732641 | Occupied | FALSE | [5 empty] | MS 05 - Coral!L35
ZLM-0356 | MS 05 | K 2,15 | 97 | Stand | 63A | ?? | 91732640 | Occupied | FALSE | [5 empty] | MS 05 - Coral!L36
ZLM-0357 | MS 05 | K 2,15 | 98 | Stand | 63A | ?? | 91732615 | Occupied | FALSE | [5 empty] | MS 05 - Coral!L37
ZLM-0358 | MS 05 | K 2,1 | Pavillion | Common / other | 350A | RWB | 91073894 | Occupied | FALSE | [5 empty] | MS 05 - Coral!AF37
ZLM-0359 | MS 05 | K 2,1 | Borehole | Common / other | 20A | RWB |  | Occupied | FALSE | [5 empty] | MS 05 - Coral!AF38
ZLM-0360 | MS 05 | K 2,1 | HW | Common / other | 20A | RWB |  | Occupied | FALSE | [5 empty] | MS 05 - Coral!AF39
ZLM-0361 | MS 05 | K 2,1 | Plant Room | Common / other | 80A | RWB |  | Occupied | FALSE | [5 empty] | MS 05 - Coral!AF40
ZLM-0362 | MS 05 | K 2,7 | 15 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!G40
ZLM-0363 | MS 05 | K 2,7 | 16 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!G41
ZLM-0364 | MS 05 | K 2,7 | 17 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!G42
ZLM-0365 | MS 05 | K 2,7 | 32 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!G43
ZLM-0366 | MS 05 | K 2,7 | 32B | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!G44
ZLM-0367 | MS 05 | K 2,7 | 27 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!G45
ZLM-0368 | MS 05 | K 2,7 | 28 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!G46
ZLM-0369 | MS 05 | K 2,7 | 29 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!G47
ZLM-0370 | MS 05 | K 2,7 | 30 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!G48
ZLM-0371 | MS 05 | K 2,11 | 44B | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!Q40
ZLM-0372 | MS 05 | K 2,11 | 45 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!Q41
ZLM-0373 | MS 05 | K 2,11 | Streetlights | Common / other | 10A | RWB |  | Unknown | FALSE | [5 empty] | MS 05 - Coral!Q42
ZLM-0374 | MS 05 | K 2,16 | 99 | Stand | 63A | ?? | 91732612 | Occupied | FALSE | [5 empty] | MS 05 - Coral!L42
ZLM-0375 | MS 05 | K 2,16 | 100 | Stand | 63A | ?? | 91732638 | Occupied | FALSE | [5 empty] | MS 05 - Coral!L43
ZLM-0376 | MS 05 | K 2,16 | 101 | Stand | 63A | ?? | 91732610 | Occupied | FALSE | [5 empty] | MS 05 - Coral!L44
ZLM-0377 | MS 05 | K 2,16 | 102 | Stand | 63A | ?? | 91732607 | Occupied | FALSE | [5 empty] | MS 05 - Coral!L45
ZLM-0378 | MS 05 | K 2,12 | 48 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!Q47
ZLM-0379 | MS 05 | K 2,12 | 49 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!Q48
ZLM-0380 | MS 05 | K 2,12 | 50 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!Q49
ZLM-0381 | MS 05 | K 2,12 | 57 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!Q50
ZLM-0382 | MS 05 | K 2,12 | 58 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!Q51
ZLM-0383 | MS 05 | K 2,12 | 59 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!Q52
ZLM-0384 | MS 05 | K 2,19 | 107 | Stand | 63A | ?? | 91732647 | Occupied | FALSE | [5 empty] | MS 05 - Coral!L52
ZLM-0385 | MS 05 | K 2,19 | 108 | Stand | 63A | ?? | 91732651 | Occupied | FALSE | [5 empty] | MS 05 - Coral!L53
ZLM-0386 | MS 05 | K 2,19 | 109 | Stand | 63A | ?? | 91732561 | Occupied | FALSE | [5 empty] | MS 05 - Coral!L54
ZLM-0387 | MS 05 | K 2,19 | 110 | Stand | 63A | ?? | 91732611 | Occupied | FALSE | [5 empty] | MS 05 - Coral!L55
ZLM-0388 | MS 05 | K 2,8 | 18 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!G53
ZLM-0389 | MS 05 | K 2,8 | 19 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!G54
ZLM-0390 | MS 05 | K 2,8 | 20 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!G55
ZLM-0391 | MS 05 | K 2,8 | 21 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!G56
ZLM-0392 | MS 05 | K 2,8 | 22 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!G57
ZLM-0393 | MS 05 | K 2,8 | 23 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!G58
ZLM-0394 | MS 05 | K 2,8 | 24 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!G59
ZLM-0395 | MS 05 | K 2,8 | 25 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!G60
ZLM-0396 | MS 05 | K 2,8 | 26 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!G61
ZLM-0397 | MS 05 | K 2,13 | 51 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!Q57
ZLM-0398 | MS 05 | K 2,13 | 52 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!Q58
ZLM-0399 | MS 05 | K 2,13 | 53 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!Q59
ZLM-0400 | MS 05 | K 2,13 | 54 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!Q60
ZLM-0401 | MS 05 | K 2,13 | 55 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!Q61
ZLM-0402 | MS 05 | K 2,13 | 56 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!Q62
ZLM-0403 | MS 05 | K 2,13 | 80 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!Q63
ZLM-0404 | MS 05 | K 2,17 | 73 | Stand | 63A | ?? | 91732539 | Occupied | FALSE | [5 empty] | MS 05 - Coral!L60
ZLM-0405 | MS 05 | K 2,17 | 74 | Stand | 63A | ?? | 91732543 | Occupied | FALSE | [5 empty] | MS 05 - Coral!L61
ZLM-0406 | MS 05 | K 2,17 | 76 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!L62
ZLM-0407 | MS 05 | K 2,17 | 77 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!L63
ZLM-0408 | MS 05 | K 2,17 | 86 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!L64
ZLM-0409 | MS 05 | K 2,18 | 53B | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!L71
ZLM-0410 | MS 05 | K 2,18 | 78 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!L72
ZLM-0411 | MS 05 | K 2,18 | 79 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!L73
ZLM-0412 | MS 05 | K 2,18 | 81 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!L74
ZLM-0413 | MS 05 | K 2,18 | 82 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!L75
ZLM-0414 | MS 05 | K 2,18 | 83 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!L76
ZLM-0415 | MS 05 | K 2,18 | 84 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!L77
ZLM-0416 | MS 05 | K 2,18 | 85 | Stand | 63A | - |  | Under construction | FALSE | [5 empty] | MS 05 - Coral!L78
ZLM-0417 | MS 05 | K 2,20 | 75 | Stand | 63A | - | 91732508 | Occupied | FALSE | [5 empty] | MS 05 - Coral!L83
ZLM-0418 | MS 05 | K 2,20 | 103 | Stand | 63A | - | 91733009 | Occupied | FALSE | [5 empty] | MS 05 - Coral!L84
ZLM-0419 | MS 05 | K 2,20 | 104 | Stand | 63A | - | 91732580 | Occupied | FALSE | [5 empty] | MS 05 - Coral!L85
ZLM-0420 | MS 05 | K 2,20 | 105 | Stand | 63A | - | 91732601 | Occupied | FALSE | [5 empty] | MS 05 - Coral!L86
ZLM-0421 | MS 05 | K 2,20 | 106 | Stand | 63A | - | 91732544 | Occupied | FALSE | [5 empty] | MS 05 - Coral!L87
ZLM-0422 | MS 05 | MS LV board | Streetlights 2,1 | Common / other | 60A | RWB? |  | Occupied | FALSE | [5 empty] | MS 05 - Coral!row 10
ZLM-0423 | MS 06 | K 4,3 | 1351 | Stand | 50A | R | 87778314 | Occupied | FALSE |  |  |  |  | Order 1 | MS 06!G16
ZLM-0424 | MS 06 | K 4,3 | 1352 | Stand | 50A | W | 85354370 | Occupied | FALSE |  |  |  |  | Order 1 | MS 06!G17
ZLM-0425 | MS 06 | K 4,3 | 1353 | Stand | 50A | B | 70694899 | Occupied | FALSE |  |  |  |  | Order 1 | MS 06!G18
ZLM-0426 | MS 06 | K 4,3 | ??? | Stand | 50A | - |  | Vacant | FALSE |  |  |  |  | Order 1 | MS 06!G19 | Placeholder slot
ZLM-0427 | MS 06 | K 4,4 | 1340 | Stand | 50A | R | 85354207 | Occupied | FALSE |  |  |  |  | Order 1 | MS 06!V16
ZLM-0428 | MS 06 | K 4,4 | 1341 | Stand | 50A | W | 84340933 | Occupied | FALSE |  |  |  |  | Order 1 | MS 06!V17
ZLM-0429 | MS 06 | K 4,4 | 1342 | Stand | 50A | B | 87778344 | Occupied | FALSE |  |  |  |  | Order 1 | MS 06!V18
ZLM-0430 | MS 06 | K 4,4 | ??? | Stand | 50A | - |  | Vacant | FALSE |  |  |  |  | Order 1 | MS 06!V19 | Placeholder slot
ZLM-0431 | MS 06 | 498 Monyana K 1,1 | 498-01 | Stand | 50A | R | 70695178 | Occupied | FALSE |  |  |  |  | Order 1 | MS 06!AA19
ZLM-0432 | MS 06 | 498 Monyana K 1,1 | 498-03 | Stand | 50A | W | 70694876 | Occupied | FALSE |  |  |  |  | Order 1 | MS 06!AA20
ZLM-0433 | MS 06 | 498 Monyana K 1,1 | 498-05 | Stand | 50A | B | 70695202 | Occupied | FALSE |  |  |  |  | Order 1 | MS 06!AA21
ZLM-0434 | MS 06 | HL – 1350 Marula (via LV K4,1) | 1350-01 | Stand | 50A | W | 90007893 | Occupied | TRUE | 2cf7f12052601205 | 2 | ZLM 1350 - 1 [Marula] | 10/5/2026, 11:52 AM |  | MS 06!L21
ZLM-0435 | MS 06 | HL – 1350 Marula (via LV K4,1) | 1350-02 | Stand | 50A | R | 90007956 | Occupied | TRUE | 2cf7f12052601205 | 1 | ZLM 1350 - 2 [Marula] | 10/5/2026, 11:52 AM |  | MS 06!L22
ZLM-0436 | MS 06 | HL – 1350 Marula (via LV K4,1) | 1350-03 | Stand | 50A | B | 90007960 | Occupied | TRUE | 2cf7f12052601205 | 3 | ZLM 1350 - 3 [Marula] | 9/22/2026, 01:05 AM |  | MS 06!L23 | No comms since 9/22/2026
ZLM-0437 | MS 06 | HL – 1350 Marula (via LV K4,1) | 1350-04 | Stand | 50A | R | 90007858 | Occupied | TRUE | 2cf7f12052601205 | 4 | ZLM 1350 - 4 [Marula] | 10/5/2026, 11:52 AM |  | MS 06!L24
ZLM-0438 | MS 06 | HL – 1350 Marula (via LV K4,1) | 1350-05 | Stand | 50A | W | 90007901 | Occupied | TRUE | 2cf7f12052601205 | 5 | ZLM 1350 - 5 [Marula] | 10/5/2026, 11:52 AM |  | MS 06!L25
ZLM-0439 | MS 06 | HL – 1350 Marula (via LV K4,1) | 1350-06 | Stand | 50A | B | 90007913 | Occupied | TRUE | 2cf7f12052601205 | 6 | ZLM 1350 - 6 [Marula] | 9/22/2026, 01:05 AM |  | MS 06!L26 | No comms since 9/22/2026
ZLM-0440 | MS 06 | HL – 1350 Marula (via LV K4,1) | 1350-07 | Stand | 50A | R | 90007961 | Occupied | TRUE | 2cf7f12052601205 | 7 | ZLM 1350 - 7 [Marula] | 10/5/2026, 11:52 AM |  | MS 06!L27
ZLM-0441 | MS 06 | HL – 1350 Marula (via LV K4,1) | 1350-08 | Stand | 50A | W | 90007905 | Occupied | TRUE | 2cf7f12052601205 | 8 | ZLM 1350 - 8 [Marula] | 10/5/2026, 11:52 AM |  | MS 06!L28
ZLM-0442 | MS 06 | HL – 1350 Marula (via LV K4,1) | 1350-09 | Stand | 50A | B | 90007948 | Occupied | TRUE | 2cf7f12052601205 | 9 | ZLM 1350 - 9 [Marula] | 10/4/2026, 11:17 AM |  | MS 06!L29
ZLM-0443 | MS 06 | HL – 1350 Marula (via LV K4,1) | 1350-10 | Stand | 50A | R | 90007863 | Occupied | FALSE |  |  |  |  | Order 1 | MS 06!L30
ZLM-0444 | MS 06 | HL – 1350 Marula (via LV K4,1) | 1350-11 | Stand | 50A | W | 90007946 | Occupied | FALSE |  |  |  |  | Order 1 | MS 06!L31
ZLM-0445 | MS 06 | HL – 1350 Marula (via LV K4,1) | 1350-12 | Stand | 50A | B | 90007923 | Occupied | TRUE | 2cf7f12052601205 | 10 | ZLM 1350 - 10 [Marula] | 10/4/2026, 11:17 AM |  | MS 06!L32 | AMR label "1350 - 10" but sheet has 1350-12
ZLM-0446 | MS 06 | HL – 1350 Marula (via LV K4,1) | Communal | Common / other | 40A | R | 42607479 | Occupied | FALSE |  |  |  |  | Order 1 | MS 06!L33
ZLM-0447 | MS 06 | HL – 1356 Highline (via LV K5,1) | 1356-01 | Stand | 63A | R | 89391863 | Occupied | TRUE | 2cf7f1205260267a | 1 | ZLM 1356 - 1 [Highline] | 8/27/2026, 03:23 AM |  | MS 06!Q21 | No comms since 8/27/2026
ZLM-0448 | MS 06 | HL – 1356 Highline (via LV K5,1) | 1356-02 | Stand | 63A | R | 89391864 | Occupied | TRUE | 2cf7f1205260267a | 2 | ZLM 1356 - 2 [Highline] | 10/4/2026, 05:47 PM |  | MS 06!Q22
ZLM-0449 | MS 06 | HL – 1356 Highline (via LV K5,1) | 1356-03 | Stand | 63A | R | 89391873 | Occupied | TRUE | 2cf7f1205260267a | 3 | ZLM 1356 - 3 [Highline] | 10/4/2026, 05:47 PM |  | MS 06!Q23
ZLM-0450 | MS 06 | HL – 1356 Highline (via LV K5,1) | 1356-04 | Stand | 63A | R | 89391874 | Occupied | TRUE | 2cf7f1205260267a | 4 | ZLM 1356 - 4 [Highline] | 10/4/2026, 05:47 PM |  | MS 06!Q24
ZLM-0451 | MS 06 | HL – 1356 Highline (via LV K5,1) | 1356-05 | Stand | 63A | W | 89391875 | Occupied | TRUE | 2cf7f1205260267a | 5 | ZLM 1356 - 5 [Highline] | 10/4/2026, 05:47 PM |  | MS 06!Q25
ZLM-0452 | MS 06 | HL – 1356 Highline (via LV K5,1) | 1356-06 | Stand | 63A | W | 89391876 | Occupied | TRUE | 2cf7f1205260267a | 6 | ZLM 1356 - 6 [Highline] | 10/4/2026, 05:47 PM |  | MS 06!Q26
ZLM-0453 | MS 06 | HL – 1356 Highline (via LV K5,1) | 1356-07 | Stand | 63A | W | 89391878 | Occupied | TRUE | 2cf7f1205260267a | 7 | ZLM 1356 - 7 [Highline] | 10/4/2026, 05:47 PM |  | MS 06!Q27
ZLM-0454 | MS 06 | HL – 1356 Highline (via LV K5,1) | 1356-08 | Stand | 63A | W | 89391880 | Occupied | TRUE | 2cf7f1205260267a | 8 | ZLM 1356 - 8 [Highline] | 10/4/2026, 05:47 PM |  | MS 06!Q28
ZLM-0455 | MS 06 | HL – 1356 Highline (via LV K5,1) | 1356-09 | Stand | 63A | B | 89391882 | Occupied | TRUE | 2cf7f1205260267a | 9 | ZLM 1356 - 9 [Highline] | 10/5/2026, 08:38 AM |  | MS 06!Q29
ZLM-0456 | MS 06 | HL – 1356 Highline (via LV K5,1) | 1356-10 | Stand | 63A | B | 89391883 | Occupied | TRUE | 2cf7f1205260267a | 10 | ZLM 1356 - 10 [Highline] | 10/5/2026, 08:38 AM |  | MS 06!Q30
ZLM-0457 | MS 06 | HL – 1356 Highline (via LV K5,1) | 1356-11 | Stand | 63A | B | 89391884 | Occupied | TRUE | 2cf7f1205260267a | 11 | ZLM 1356 - 11 [Highline] | 10/5/2026, 08:38 AM |  | MS 06!Q31
ZLM-0458 | MS 06 | HL – 1356 Highline (via LV K5,1) | 1356-12 | Stand | 63A | B | 89391885 | Occupied | TRUE | 2cf7f1205260267a | 12 | ZLM 1356 - 12 [Highline] | 10/5/2026, 08:38 AM |  | MS 06!Q32
ZLM-0459 | MS 06 | HL – 1356 Highline (via LV K5,1) | Communal | Common / other | 63A | B | 90007949 | Occupied | TRUE | 2cf7f1205260267a | 13 | ZLM 1356 - Common [Highline] | 10/5/2026, 08:38 AM |  | MS 06!Q33
ZLM-0460 | MS 06 | K 4,6 | 1354 | Stand | 50A | B | 90007878 | Occupied | FALSE |  |  |  |  | Order 1 | MS 06!V24
ZLM-0461 | MS 06 | K 4,6 | 1355 | Stand | 50A | W | 90007922 | Occupied | FALSE |  |  |  |  | Order 1 | MS 06!V25
ZLM-0462 | MS 06 | K 4,6 | ??? | Stand | 50A | - |  | Vacant | FALSE |  |  |  |  | Order 1 | MS 06!V26 | Placeholder slot
ZLM-0463 | MS 06 | K 4,6 | ??? | Stand | 50A | - |  | Vacant | FALSE |  |  |  |  | Order 1 | MS 06!V27 | Placeholder slot
ZLM-0464 | MS 06 | 498 Monyana K 1,2 | 498-02 | Stand | 50A | B | 70694901 | Occupied | FALSE |  |  |  |  | Order 1 | MS 06!AA26
ZLM-0465 | MS 06 | 498 Monyana K 1,2 | 498-04 | Stand | 50A | R | 42576456 | Occupied | FALSE |  |  |  |  | Order 1 | MS 06!AA27
ZLM-0466 | MS 06 | 498 Monyana K 1,2 | 498-06 | Stand | 50A | W | 70695174 | Occupied | FALSE |  |  |  |  | Order 1 | MS 06!AA28
ZLM-0467 | MS 06 | 498 Monyana K 1,2 | Communal | Common / other | 32A | R | 70694925 | Occupied | FALSE |  |  |  |  | Order 1 | MS 06!AA29
ZLM-0468 | MS 06 | K 4,7 | 1346 | Stand | 50A | B |  | Vacant | FALSE |  |  |  |  | Order 1 | MS 06!V32
ZLM-0469 | MS 06 | K 4,7 | 1347 | Stand | 50A | B | 87819159 | Occupied | FALSE |  |  |  |  | Order 1 | MS 06!V33
ZLM-0470 | MS 06 | K 4,7 | ??? | Stand | 50A | - |  | Vacant | FALSE |  |  |  |  | Order 1 | MS 06!V34 | Placeholder slot
ZLM-0471 | MS 06 | K 4,7 | ??? | Stand | 50A | - |  | Vacant | FALSE |  |  |  |  | Order 1 | MS 06!V35 | Placeholder slot
ZLM-0472 | MS 06 | 498 Monyana K 1,3 | 498-08A | Stand | 50A | R | 70694923 | Occupied | FALSE |  |  |  |  | Order 1 | MS 06!AA34
ZLM-0473 | MS 06 | 498 Monyana K 1,3 | 498-08B | Stand | 50A | R | 42576489 | Occupied | FALSE |  |  |  |  | Order 1 | MS 06!AA35
ZLM-0474 | MS 06 | 498 Monyana K 1,3 | 498-09A | Stand | 50A | W | 42576526 | Occupied | FALSE |  |  |  |  | Order 1 | MS 06!AA36
ZLM-0475 | MS 06 | 498 Monyana K 1,3 | 498-09B | Stand | 50A | W | 84039879 | Occupied | FALSE |  |  |  |  | Order 1 | MS 06!AA37
ZLM-0476 | MS 06 | 498 Monyana K 1,3 | 498-10A | Stand | 50A | W | 84039877 | Occupied | FALSE |  |  |  |  | Order 1 | MS 06!AA38
ZLM-0477 | MS 06 | 498 Monyana K 1,3 | 498-10B | Stand | 50A | R | 84039882 | Occupied | FALSE |  |  |  |  | Order 1 | MS 06!AA39
ZLM-0478 | MS 06 | 498 Monyana K 1,3 | 498-11A | Stand | 50A | B | 84039885 | Occupied | FALSE |  |  |  |  | Order 1 | MS 06!AA40
ZLM-0479 | MS 06 | 498 Monyana K 1,3 | 498-11B | Stand | 50A | B | 42576532 | Occupied | FALSE |  |  |  |  | Order 1 | MS 06!AA41
ZLM-0480 | MS 06 | 498 Monyana K 1,4 | 498-07 | Stand | 50A | R | 84340910 | Occupied | FALSE |  |  |  |  | Order 1 | MS 06!AA46
ZLM-0481 | MS 06 | 498 Monyana K 1,4 | 498-12 | Stand | 50A | W | 84340914 | Occupied | FALSE |  |  |  |  | Order 1 | MS 06!AA47
ZLM-0482 | MS 06 | 498 Monyana K 1,5 | 498-13 | Stand | 50A | R | 84340928 | Occupied | FALSE |  |  |  |  | Order 1 | MS 06!AA52
ZLM-0483 | MS 06 | 498 Monyana K 1,5 | 498-14 | Stand | 50A | W | 84340937 | Occupied | FALSE |  |  |  |  | Order 1 | MS 06!AA53
ZLM-0484 | MS 06 | 498 Monyana K 1,5 | 498-15 | Stand | 63A | B | 84340906 | Occupied | FALSE |  |  |  |  | Order 1 | MS 06!AA54
ZLM-0485 | MS 06 | 498 Monyana Garage Kiosk | 498-1G | Stand | 20A | R | 42576456 | Occupied | FALSE |  |  |  |  | Order 1 | MS 06!AA59
ZLM-0486 | MS 06 | 498 Monyana Garage Kiosk | 498-2G | Stand | 20A | W | 42576526 | Occupied | FALSE |  |  |  |  | Order 1 | MS 06!AA60
ZLM-0487 | MS 06 | 498 Monyana Garage Kiosk | 498-3G | Stand | 20A | B | 42576489 | Occupied | FALSE |  |  |  |  | Order 1 | MS 06!AA61
ZLM-0488 | MS 06 | 498 Monyana Garage Kiosk | 498-4G | Stand | 20A | R | 84341057 | Occupied | FALSE |  |  |  |  | Order 1 | MS 06!AA62
ZLM-0489 | MS 06 | 498 Monyana Garage Kiosk | 498-5G | Stand | 20A | W | 84340911 | Occupied | FALSE |  |  |  |  | Order 1 | MS 06!AA63
ZLM-0490 | MS 06 | 498 Monyana Garage Kiosk | 498-6G | Stand | 20A | B | 84341044 | Occupied | FALSE |  |  |  |  | Order 1 | MS 06!AA64
ZLM-0491 | MS 06 | 498 Monyana Garage Kiosk | 498-7G | Stand | 20A | R | 84340955 | Occupied | FALSE |  |  |  |  | Order 1 | MS 06!AA65
ZLM-0492 | MS 06 | MS LV board | Streetlights | Common / other | 32A | RWB? | 47369899 | Occupied | FALSE | [5 empty] | MS 06!row 10 | Deferred from Order 1 (streetlight on MS board)
ZLM-0493 | MS 07 | Rem 501 V/V K1 | REM 501/01 | Stand | 63A | W | 89391891 | Occupied | FALSE |  |  |  |  | Order 1 | MS 07!L16
ZLM-0494 | MS 07 | Rem 501 V/V K1 | REM 501/02 | Stand | 63A | B | 89392157 | Occupied | FALSE |  |  |  |  | Order 1 | MS 07!L17
ZLM-0495 | MS 07 | Rem 501 V/V K1 | REM 501/03 | Stand | 63A | B | 89392110 | Occupied | FALSE |  |  |  |  | Order 1 | MS 07!L18
ZLM-0496 | MS 07 | Rem 501 V/V K1 | REM 501/04 | Stand | 63A | B | 89392103 | Occupied | FALSE |  |  |  |  | Order 1 | MS 07!L19
ZLM-0497 | MS 07 | Rem 501 V/V K1 | REM 501/05 | Stand | 63A | R | 89392105 | Occupied | FALSE |  |  |  |  | Order 1 | MS 07!L20
ZLM-0498 | MS 07 | Rem 501 V/V K1 | REM 501/06 | Stand | 63A | W | 89392101 | Occupied | FALSE |  |  |  |  | Order 1 | MS 07!L21
ZLM-0499 | MS 07 | Rem 501 V/V K1 | REM 501/07 | Stand | 63A | B | 89392149 | Occupied | FALSE |  |  |  |  | Order 1 | MS 07!L22
ZLM-0500 | MS 07 | Rem 501 V/V K1 | REM 501/08 | Stand | 63A | W | 89392113 | Occupied | FALSE |  |  |  |  | Order 1 | MS 07!L23
ZLM-0501 | MS 07 | Rem 501 V/V K1 | REM 501/09 | Stand | 63A | R | 89392106 | Occupied | FALSE |  |  |  |  | Order 1 | MS 07!L24
ZLM-0502 | MS 07 | Rem 501 V/V K1 | REM 501/10 | Stand | 63A | R | 89392117 | Occupied | FALSE |  |  |  |  | Order 1 | MS 07!L25
ZLM-0503 | MS 07 | Club House / Restaurant | Lounge DB | Common / other | 63A | R | L-CH-001 | Occupied | FALSE |  |  |  |  | Order 1 | MS 07!Q16
ZLM-0504 | MS 07 | Club House / Restaurant | Basement DB | Common / other | 63A | W | B-CH-002 | Occupied | FALSE |  |  |  |  | Order 1 | MS 07!Q17
ZLM-0505 | MS 07 | Club House / Restaurant | Upstairs DB | Common / other | 63A | B | US-CH-003 | Occupied | FALSE |  |  |  |  | Order 1 | MS 07!Q18
ZLM-0506 | MS 07 | K 1,1 | Ptn 501/01 | Stand | 63A | R | 84340908 | Occupied | FALSE |  |  |  |  | Order 1 | MS 07!G22
ZLM-0507 | MS 07 | K 1,1 | Ptn 501/02 | Stand | 63A | W | 84340913 | Occupied | FALSE |  |  |  |  | Order 1 | MS 07!G23
ZLM-0508 | MS 07 | K 1,1 | Ptn 501/03 | Stand | 63A | B | 84340904 | Occupied | FALSE |  |  |  |  | Order 1 | MS 07!G24
ZLM-0509 | MS 07 | K 1,1 | Ptn 501/04 | Stand | 63A | R | 84340686 | Occupied | FALSE |  |  |  |  | Order 1 | MS 07!G25
ZLM-0510 | MS 07 | K 1,1 | Ptn 501/05 | Stand | 63A | W | 84340952 | Occupied | FALSE |  |  |  |  | Order 1 | MS 07!G26
ZLM-0511 | MS 07 | Rem 501 V/V K2 | REM 501/11 | Stand | 63A | W | 89392104 | Occupied | FALSE |  |  |  |  | Order 1 | MS 07!L30
ZLM-0512 | MS 07 | Rem 501 V/V K2 | REM 501/12 | Stand | 63A | R | 89392131 | Occupied | FALSE |  |  |  |  | Order 1 | MS 07!L31
ZLM-0513 | MS 07 | Rem 501 V/V K2 | REM 501/13 | Stand | 63A | W | 89392132 | Occupied | FALSE |  |  |  |  | Order 1 | MS 07!L32
ZLM-0514 | MS 07 | Rem 501 V/V K2 | REM 501/14 | Stand | 63A | B | 89392109 | Occupied | FALSE |  |  |  |  | Order 1 | MS 07!L33
ZLM-0515 | MS 07 | Rem 501 V/V K2 | REM 501/15 | Stand | 63A | W | 89392102 | Occupied | FALSE |  |  |  |  | Order 1 | MS 07!L34
ZLM-0516 | MS 07 | Rem 501 V/V K2 | REM 501/16 | Stand | 63A | B | 89392136 | Occupied | FALSE |  |  |  |  | Order 1 | MS 07!L35
ZLM-0517 | MS 07 | Rem 501 V/V K2 | REM 501/17 | Stand | 63A | R | 89392127 | Occupied | FALSE |  |  |  |  | Order 1 | MS 07!L36
ZLM-0518 | MS 07 | Rem 501 V/V K2 | REM 501/18 | Stand | 63A | R | 89392140 | Occupied | FALSE |  |  |  |  | Order 1 | MS 07!L37
ZLM-0519 | MS 07 | K 1,2 | Ptn 501/06 | Stand | 63A | W |  | Under construction | FALSE |  |  |  |  | Order 1 | MS 07!G31
ZLM-0520 | MS 07 | K 1,2 | Ptn 501/07 | Stand | 63A | R | 84340593 | Occupied | FALSE |  |  |  |  | Order 1 | MS 07!G32
ZLM-0521 | MS 07 | K 1,2 | Ptn 501/08 | Stand | 63A | W | 84340708 | Occupied | FALSE |  |  |  |  | Order 1 | MS 07!G33
ZLM-0522 | MS 07 | K 1,2 | Ptn 501/09 | Stand | 63A | B | 47369117 | Occupied | FALSE |  |  |  |  | Order 1 | MS 07!G34
ZLM-0523 | MS 07 | K 1,2 | Ptn 501/10 | Stand | 63A | R | 46886469 | Occupied | FALSE |  |  |  |  | Order 1 | MS 07!G35
ZLM-0524 | MS 07 | K 2,1 | Ptn 501/11 | Stand | 63A | R | 91546482 | Occupied | FALSE |  |  |  |  | Order 1 | MS 07!G40
ZLM-0525 | MS 07 | K 2,1 | Ptn 501/12 | Stand | 63A | R | 89392169 | Occupied | FALSE |  |  |  |  | Order 1 | MS 07!G41
ZLM-0526 | MS 07 | K 2,1 | Ptn 501/13 | Stand | 63A | B | 87778358 | Occupied | FALSE |  |  |  |  | Order 1 | MS 07!G42
ZLM-0527 | MS 07 | K 2,1 | Ptn 501/14 | Stand | 63A | R | 87778380 | Occupied | FALSE |  |  |  |  | Order 1 | MS 07!G43
ZLM-0528 | MS 07 | K 2,1 | Ptn 501/15 | Stand | 63A | B | 87778386 | Occupied | FALSE |  |  |  |  | Order 1 | MS 07!G44
ZLM-0529 | MS 07 | Rem 501 V/V K3 | REM 501/19 | Stand | 63A | W | 89392139 | Occupied | TRUE | 2cf7f120526045cf | 2 | ZLM 501-19 [Valley View] | 10/5/2026, 02:13 AM |  | MS 07!L42
ZLM-0530 | MS 07 | Rem 501 V/V K3 | REM 501/20 | Stand | 63A | B | 90007952 | Occupied | TRUE | 2cf7f120526045cf | 3 | ZLM 501-20 [Valley View] | 10/5/2026, 02:13 AM |  | MS 07!L43
ZLM-0531 | MS 07 | Rem 501 V/V K3 | REM 501/21 | Stand | 63A | B | 90007857 | Occupied | TRUE | 2cf7f120526045cf | 8 | ZLM 501-21 [Valley View] | 10/5/2026, 02:13 AM |  | MS 07!L44
ZLM-0532 | MS 07 | Rem 501 V/V K3 | REM 501/22 | Stand | 63A | R | 89392173 | Occupied | TRUE | 2cf7f120526045cf | 1 | ZLM 501-22 [Valley View] | 10/5/2026, 02:13 AM |  | MS 07!L45
ZLM-0533 | MS 07 | Rem 501 V/V K3 | REM 501/23 | Stand | 63A | B | 89391877 | Occupied | TRUE | 2cf7f120526045cf | 6 | ZLM 501-23 [Valley View] | 10/5/2026, 02:13 AM |  | MS 07!L46
ZLM-0534 | MS 07 | Rem 501 V/V K3 | REM 501/24 | Stand | 63A | W | 89391866 | Occupied | TRUE | 2cf7f120526045cf | 5 | ZLM 501-24 [Valley View] | 10/5/2026, 02:13 AM |  | MS 07!L47
ZLM-0535 | MS 07 | Rem 501 V/V K3 | REM 501/25 | Stand | 63A | R | 89391865 | Occupied | TRUE | 2cf7f120526045cf | 7 | ZLM 501-25 [Valley View] | 10/5/2026, 02:13 AM |  | MS 07!L48
ZLM-0536 | MS 07 | Rem 501 V/V K3 | REM 501/26 | Stand | 63A | R | 89392135 | Occupied | TRUE | 2cf7f120526045cf | 4 | ZLM 501-26 [Valley View] | 10/5/2026, 02:13 AM |  | MS 07!L49
ZLM-0537 | MS 07 | K 2,2 | Ptn 501/16 | Stand | 63A | R | 85353960 | Occupied | FALSE |  |  |  |  | Order 1 | MS 07!G49
ZLM-0538 | MS 07 | K 2,2 | Ptn 501/17 | Stand | 63A | R | 85354417 | Occupied | FALSE |  |  |  |  | Order 1 | MS 07!G50
ZLM-0539 | MS 07 | K 2,2 | Ptn 501/18 | Stand | 63A | R | 85354403 | Occupied | FALSE |  |  |  |  | Order 1 | MS 07!G51
ZLM-0540 | MS 07 | K 2,2 | Ptn 501/19 | Stand | 63A | B | 84039931 | Occupied | FALSE |  |  |  |  | Order 1 | MS 07!G52
ZLM-0541 | MS 07 | K 2,2 | Ptn 501/20 | Stand | 63A | W | 85354390 | Occupied | FALSE |  |  |  |  | Order 1 | MS 07!G53
ZLM-0542 | MS 07 | MS LV board | Streetlights | Common / other | 63A | RWB? | 82929432 | Occupied | FALSE | [5 empty] | MS 07!row 10 | Deferred from Order 1 (streetlight on MS board)
ZLM-0543 | MS 08 | 503 Reserve K503 | 503-01 | Stand | 63A | B | 87778583 | Occupied | FALSE | [5 empty] | MS 08!G16
ZLM-0544 | MS 08 | 503 Reserve K503 | 503-02 | Stand | 63A | W | 90007809 | Occupied | FALSE | [5 empty] | MS 08!G17
ZLM-0545 | MS 08 | 503 Reserve K503 | 503-03 | Stand | 63A | R | 84039888 | Occupied | FALSE | [5 empty] | MS 08!G18
ZLM-0546 | MS 08 | 503 Reserve KO | 503-04 | Stand | 63A | B | 87819235 | Occupied | FALSE | [5 empty] | MS 08!B22
ZLM-0547 | MS 08 | 503 Reserve KO | 503-05 | Stand | 63A | R | 87819216 | Occupied | FALSE | [5 empty] | MS 08!B23
ZLM-0548 | MS 08 | 503 Reserve KO | 503-06 | Stand | 63A | W | 87819464 | Occupied | FALSE | [5 empty] | MS 08!B24
ZLM-0549 | MS 08 | 503 Reserve KO | 503-07 | Stand | 63A | B | 87819168 | Occupied | FALSE | [5 empty] | MS 08!B25
ZLM-0550 | MS 08 | 503 Reserve KO | S/LIGHTS | Common / other | 15A | W |  | Occupied | FALSE | [5 empty] | MS 08!B26
ZLM-0551 | MS 08 | 503 Reserve KP | 503-08 | Stand | 63A | W | 87819416 | Occupied | FALSE | [5 empty] | MS 08!B31
ZLM-0552 | MS 08 | 503 Reserve KP | 503-09 | Stand | 63A | B | 87819288 | Occupied | FALSE | [5 empty] | MS 08!B32
ZLM-0553 | MS 08 | 503 Reserve KP | 503-10 | Stand | 63A | R | 91546006 | Occupied | FALSE | [5 empty] | MS 08!B33
ZLM-0554 | MS 08 | 503 Reserve KP | 503-11 | Stand | 63A | R | 91546463 | Occupied | FALSE | [5 empty] | MS 08!B34
ZLM-0555 | MS 08 | 503 Reserve KP | S/LIGHTS | Common / other | 15A | B |  | Occupied | FALSE | [5 empty] | MS 08!B35
ZLM-0556 | MS 08 | 503 Reserve KQ | 503-12 | Stand | 63A | R | 91546868 | Occupied | FALSE | [5 empty] | MS 08!B40
ZLM-0557 | MS 08 | 503 Reserve KQ | 503-13 | Stand | 63A | W | 91546128 | Occupied | FALSE | [5 empty] | MS 08!B41
ZLM-0558 | MS 08 | 503 Reserve KQ | 503-14 | Stand | 63A | B | 91733261 | Occupied | FALSE | [5 empty] | MS 08!B42
ZLM-0559 | MS 08 | 503 Reserve KQ | 503 - Builder | Stand | 63A | R | 91733419 | Under construction | FALSE | [5 empty] | MS 08!B43
ZLM-0560 | MS 08 | 503 Reserve KQ | S/LIGHTS | Common / other | 15A | - |  | Vacant | FALSE | [5 empty] | MS 08!B44
ZLM-0561 | MS 09 | K 9,4 | 1269 | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 09!Q16
ZLM-0562 | MS 09 | K 9,4 | 1270 | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 09!Q17
ZLM-0563 | MS 09 | K 9,4 | 1271 | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 09!Q18
ZLM-0564 | MS 09 | K 9,4 | 1272 | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 09!Q19
ZLM-0565 | MS 09 | K 9,3 | 1266 | Stand | 63A | B | 85354354 | Occupied | FALSE | [5 empty] | MS 09!V16
ZLM-0566 | MS 09 | K 9,3 | 1267 | Stand | 63A | B | 91546472 | Under construction | FALSE | [5 empty] | MS 09!V17
ZLM-0567 | MS 09 | K 9,3 | 1265 | Stand | 63A | W | 91732541 | Under construction | FALSE | [5 empty] | MS 09!V18
ZLM-0568 | MS 09 | K 9,3 | 1264 | Stand | 63A | R | 68054424 | Under construction | FALSE | [5 empty] | MS 09!V19
ZLM-0569 | MS 09 | K 9,3 | ??? | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 09!V20 | Placeholder slot
ZLM-0570 | MS 09 | K 9,9 | 1277 | Stand | 63A | R | 75091255 | Occupied | FALSE | [5 empty] | MS 09!AA16
ZLM-0571 | MS 09 | K 9,9 | 1293 | Stand | 63A | B | 75091154 | Occupied | FALSE | [5 empty] | MS 09!AA17
ZLM-0572 | MS 09 | K 9,9 | 1292 | Stand | 63A | B | 91733076 | Under construction | FALSE | [5 empty] | MS 09!AA18
ZLM-0573 | MS 09 | K 9,9 | 1291 | Stand | 63A | W | 91733025 | Under construction | FALSE | [5 empty] | MS 09!AA19
ZLM-0574 | MS 09 | K 9,5 | 1273 | Stand | 63A | R | 85354420 | Occupied | FALSE | [5 empty] | MS 09!Q24
ZLM-0575 | MS 09 | K 9,5 | 1274 | Stand | 63A | W | 91546480 | Under construction | FALSE | [5 empty] | MS 09!Q25
ZLM-0576 | MS 09 | K 9,5 | ??? | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 09!Q26 | Placeholder slot
ZLM-0577 | MS 09 | K 9,5 | ??? | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 09!Q27 | Placeholder slot
ZLM-0578 | MS 09 | K 9,8 | 1279 | Stand | 63A | W | 85354374 | Occupied | FALSE | [5 empty] | MS 09!AA24
ZLM-0579 | MS 09 | K 9,8 | 1289 | Stand | 63A | B | 85354368 | Occupied | FALSE | [5 empty] | MS 09!AA25
ZLM-0580 | MS 09 | K 9,8 | 1278 | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 09!AA26
ZLM-0581 | MS 09 | K 9,8 | 1290 | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 09!AA27
ZLM-0582 | MS 09 | K 9,2 | 1260 | Stand | 63A | R | 42607786 | Occupied | FALSE | [5 empty] | MS 09!V25
ZLM-0583 | MS 09 | K 9,2 | 1261 | Stand | 63A | W | 85353984 | Under construction | FALSE | [5 empty] | MS 09!V26
ZLM-0584 | MS 09 | K 9,2 | 1262 | Stand | 63A | B | 75091235 | Occupied | FALSE | [5 empty] | MS 09!V27
ZLM-0585 | MS 09 | K 9,2 | 1263 | Stand | 63A | W | 75091230 | Occupied | FALSE | [5 empty] | MS 09!V28
ZLM-0586 | MS 09 | K 9,2 | ??? | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 09!V29 | Placeholder slot
ZLM-0587 | MS 09 | K 9,7 | 1280 | Stand | 63A | R | 87778399 | Occupied | FALSE | [5 empty] | MS 09!AA32
ZLM-0588 | MS 09 | K 9,7 | 1281 | Stand | 63A | W | 87778397 | Occupied | FALSE | [5 empty] | MS 09!AA33
ZLM-0589 | MS 09 | K 9,7 | 1287 | Stand | 63A | B | 84340930 | Occupied | FALSE | [5 empty] | MS 09!AA34
ZLM-0590 | MS 09 | K 9,7 | 1288 | Stand | 63A | B | 75091290 | Occupied | FALSE | [5 empty] | MS 09!AA35
ZLM-0591 | MS 09 | K 9,1 | 1255 | Stand | 63A | R | 84340903 | Occupied | FALSE | [5 empty] | MS 09!V34
ZLM-0592 | MS 09 | K 9,1 | 1256 | Stand | 63A | W | 42607477 | Occupied | FALSE | [5 empty] | MS 09!V35
ZLM-0593 | MS 09 | K 9,1 | 1259 | Stand | 63A | B | 85354286 | Occupied | FALSE | [5 empty] | MS 09!V36
ZLM-0594 | MS 09 | K 9,1 | 1258 | Stand | 63A | R |  | Vacant | FALSE | [5 empty] | MS 09!V37
ZLM-0595 | MS 09 | K 9,6 | 1282 | Stand | 63A | R | 85354239 | Occupied | FALSE | [5 empty] | MS 09!AA40
ZLM-0596 | MS 09 | K 9,6 | 1283 | Stand | 63A | W | 90007889 | Occupied | FALSE | [5 empty] | MS 09!AA41
ZLM-0597 | MS 09 | K 9,6 | 1284 | Stand | 63A | B | 75091124 | Occupied | FALSE | [5 empty] | MS 09!AA42
ZLM-0598 | MS 09 | K 9,6 | 1285 | Stand | 63A | R | 47369244 | Occupied | FALSE | [5 empty] | MS 09!AA43
ZLM-0599 | MS 09 | K 9,6 | 1286 | Stand | 63A | W | 91546275 | Under construction | FALSE | [5 empty] | MS 09!AA44
ZLM-0600 | MS 09 | MS LV board | Sewer Pump Station | Common / other | 100A | RWB? | 83014662 | Occupied | FALSE | [5 empty] | MS 09!row 10
ZLM-0601 | MS 09 | MS LV board | Pump Station | Common / other | 100A | RWB? | 47369892 | Occupied | FALSE | [5 empty] | MS 09!row 10
ZLM-0602 | MS 09 | MS LV board | Streetlights | Common / other | 60A | RWB? | 47369910 | Occupied | FALSE | [5 empty] | MS 09!row 10
ZLM-0603 | MS 10 | K 10,1 | 1150 | Stand | 63A | R | 72404391 | Occupied | FALSE | [5 empty] | MS 10!L16
ZLM-0604 | MS 10 | K 10,1 | 1151 | Stand | 63A | W | 84340925 | Occupied | FALSE | [5 empty] | MS 10!L17
ZLM-0605 | MS 10 | K 10,1 | 1126 | Stand | 63A | B | 77308414 | Occupied | FALSE | [5 empty] | MS 10!L18
ZLM-0606 | MS 10 | K 10,1 | 1127 | Stand | 63A | R | 91546311 | Under construction | FALSE | [5 empty] | MS 10!L19
ZLM-0607 | MS 10 | K 10,2 | 1706-01 | Stand | 63A | R | 75091289 | Occupied | FALSE | [5 empty] | MS 10!Q16
ZLM-0608 | MS 10 | K 10,2 | 1704 | Stand | 80A | RWB | 90151407 | Occupied | FALSE | [5 empty] | MS 10!Q17
ZLM-0609 | MS 10 | K 10,2 | 1143 | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 10!Q18
ZLM-0610 | MS 10 | K 10,2 | 1128 | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 10!Q19
ZLM-0611 | MS 10 | K 10,2 | 1706-02 | Stand | 63A | W | 91546074 | Occupied | FALSE | [5 empty] | MS 10!Q20
ZLM-0612 | MS 10 | K 10,7 | 1146 | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 10!V16
ZLM-0613 | MS 10 | K 10,7 | 1147 | Stand | 63A | W | 91733399 | Occupied | FALSE | [5 empty] | MS 10!V17
ZLM-0614 | MS 10 | K 10,7 | 1148 | Stand | 63A | B | 84340935 | Occupied | FALSE | [5 empty] | MS 10!V18
ZLM-0615 | MS 10 | K 10,7 | 1149 | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 10!V19
ZLM-0616 | MS 10 | K 10,9 | 1121 | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 10!AA16
ZLM-0617 | MS 10 | K 10,9 | 1122 | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 10!AA17
ZLM-0618 | MS 10 | K 10,9 | 1123 | Stand | 63A | B | 87778406 | Occupied | FALSE | [5 empty] | MS 10!AA18
ZLM-0619 | MS 10 | K 10,9 | 1124 | Stand | 63A | W | 85353985 | Occupied | FALSE | [5 empty] | MS 10!AA19
ZLM-0620 | MS 10 | K 10,9 | 1125 | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 10!AA20
ZLM-0621 | MS 10 | K 10,8 | 1152 | Stand | 63A | W | 72404386 | Occupied | FALSE | [5 empty] | MS 10!L24
ZLM-0622 | MS 10 | K 10,8 | 1153 | Stand | 63A | R | 71205273 | Occupied | FALSE | [5 empty] | MS 10!L25
ZLM-0623 | MS 10 | K 10,8 | 1154 | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 10!L26
ZLM-0624 | MS 10 | K 10,8 | 1155 | Stand | 63A | B | 84340909 | Occupied | FALSE | [5 empty] | MS 10!L27
ZLM-0625 | MS 10 | K 10,8 | 1156 | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 10!L28
ZLM-0626 | MS 10 | K 10,6 | 1139 | Stand | 63A | R | 84039918 | Occupied | FALSE | [5 empty] | MS 10!V24
ZLM-0627 | MS 10 | K 10,6 | 1140 | Stand | 63A | W | 87778582 | Occupied | FALSE | [5 empty] | MS 10!V25
ZLM-0628 | MS 10 | K 10,6 | 1141 | Stand | 63A | B | 75091224 | Occupied | FALSE | [5 empty] | MS 10!V26
ZLM-0629 | MS 10 | K 10,6 | 1706 - 09 | Stand | 63A | W | 84340912 | Occupied | FALSE | [5 empty] | MS 10!V27
ZLM-0630 | MS 10 | K 10,6 | 1706 - 08 | Stand | 63A | R | 42576436 | Occupied | FALSE | [5 empty] | MS 10!V28
ZLM-0631 | MS 10 | K 10,3 | 1131 | Stand | 63A | R | 85354273 | Occupied | FALSE | [5 empty] | MS 10!Q25
ZLM-0632 | MS 10 | K 10,3 | 1130 | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 10!Q26
ZLM-0633 | MS 10 | K 10,3 | 1706-04 | Stand | 63A | W | 42576495 | Occupied | FALSE | [5 empty] | MS 10!Q27
ZLM-0634 | MS 10 | K 10,3 | 1145 | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 10!Q28
ZLM-0635 | MS 10 | K 10,3 | 1706-05 | Stand | 63A | B | 87819187 | Occupied | FALSE | [5 empty] | MS 10!Q29
ZLM-0636 | MS 10 | K 10,3 | 1706-03 | Stand | 63A | B | 91546492 | Occupied | FALSE | [5 empty] | MS 10!Q30
ZLM-0637 | MS 10 | K 10,10 | 1116 | Stand | 63A | R | 71205179 | Occupied | FALSE | [5 empty] | MS 10!AA25
ZLM-0638 | MS 10 | K 10,10 | 1117 | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 10!AA26
ZLM-0639 | MS 10 | K 10,10 | 1118 | Stand | 63A | B | 47369121 | Occupied | FALSE | [5 empty] | MS 10!AA27
ZLM-0640 | MS 10 | K 10,10 | 1119 | Stand | 63A | R | 62627200 | Occupied | FALSE | [5 empty] | MS 10!AA28
ZLM-0641 | MS 10 | K 10,10 | 1120 | Stand | 63A | B | 84039727 | Under construction | FALSE | [5 empty] | MS 10!AA29
ZLM-0642 | MS 10 | K 10,5 | 1706-07 | Stand | 63A | R | 47369135 | Occupied | FALSE | [5 empty] | MS 10!V33
ZLM-0643 | MS 10 | K 10,5 | 1706-06 | Stand | 63A | W | 47511107 | Occupied | FALSE | [5 empty] | MS 10!V34
ZLM-0644 | MS 10 | K 10,5 | 1137 | Stand | 63A | B | 91546267 | Under construction | FALSE | [5 empty] | MS 10!V35
ZLM-0645 | MS 10 | K 10,5 | ??? | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 10!V36 | Placeholder slot
ZLM-0646 | MS 10 | K 10,5 | ??? | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 10!V37 | Placeholder slot
ZLM-0647 | MS 10 | K 10,4 | 1132 | Stand | 63A | R | 46884750 | Occupied | FALSE | [5 empty] | MS 10!Q35
ZLM-0648 | MS 10 | K 10,4 | 1133 | Stand | 63A | W | 84340951 | Occupied | FALSE | [5 empty] | MS 10!Q36
ZLM-0649 | MS 10 | K 10,4 | 1134 | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 10!Q37
ZLM-0650 | MS 10 | K 10,4 | 1135 | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 10!Q38
ZLM-0651 | MS 10 | MS LV board | Sewer Pump Station | Common / other | 200A | RWB? | 83014678 | Occupied | FALSE | [5 empty] | MS 10!row 10
ZLM-0652 | MS 10 | MS LV board | Streetlights Kiosk | Common / other | 63A | RWB? | 42866560 | Occupied | FALSE | [5 empty] | MS 10!row 10
ZLM-0653 | MS 11 | K 11,4 | 1246 | Stand | 63A | W | 91732973 | Under construction | FALSE | [5 empty] | MS 11!G16
ZLM-0654 | MS 11 | K 11,4 | 1247 | Stand | 63A | RWB | 98819665 | Under construction | FALSE | [5 empty] | MS 11!G17
ZLM-0655 | MS 11 | K 11,4 | 1248 | Stand | 63A | R | 91546466 | Occupied | FALSE | [5 empty] | MS 11!G18
ZLM-0656 | MS 11 | K 11,4 | 1215 | Stand | 63A | B | 89392172 | Under construction | FALSE | [5 empty] | MS 11!G19
ZLM-0657 | MS 11 | K 11,4 | 1216 | Stand | 63A | B | 75091339 | Occupied | FALSE | [5 empty] | MS 11!G20
ZLM-0658 | MS 11 | K 11,5 | 1244 | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 11!L16
ZLM-0659 | MS 11 | K 11,5 | 1245 | Stand | 63A | B | 84340932 | Occupied | FALSE | [5 empty] | MS 11!L17
ZLM-0660 | MS 11 | K 11,5 | 1218 | Stand | 63A | W | 89392168 | Occupied | FALSE | [5 empty] | MS 11!L18
ZLM-0661 | MS 11 | K 11,5 | 1219 | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 11!L19
ZLM-0662 | MS 11 | K 11,5 | 1220 | Stand | 63A | R | 87819063 | Occupied | FALSE | [5 empty] | MS 11!L20
ZLM-0663 | MS 11 | K 11,5 | 1217 | Stand | 63A | R | 46886446 | Occupied | FALSE | [5 empty] | MS 11!L21
ZLM-0664 | MS 11 | K 11,2 | 1250 | Stand | 63A | B | 91546442 | Occupied | FALSE | [5 empty] | MS 11!Q16
ZLM-0665 | MS 11 | K 11,2 | 1251 | Stand | 63A | W | 42606924 | Occupied | FALSE | [5 empty] | MS 11!Q17
ZLM-0666 | MS 11 | K 11,2 | ??? | Stand | 63A | B |  | Vacant | FALSE | [5 empty] | MS 11!Q18 | Placeholder slot
ZLM-0667 | MS 11 | K 11,2 | 1161 | Stand | 80A | W | 85354204 | Occupied | FALSE | [5 empty] | MS 11!Q19
ZLM-0668 | MS 11 | K 11,2 | 1162 | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 11!Q20
ZLM-0669 | MS 11 | K 11,8 | 1240 | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 11!V16
ZLM-0670 | MS 11 | K 11,8 | 1239 | Stand | 63A | R | 91546192 | Under construction | FALSE | [5 empty] | MS 11!V17
ZLM-0671 | MS 11 | K 11,8 | 1238 | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 11!V18
ZLM-0672 | MS 11 | K 11,8 | 1227 | Stand | 63A | B | 91732582 | Under construction | FALSE | [5 empty] | MS 11!V19
ZLM-0673 | MS 11 | K 11,8 | 1237 | Stand | 63A | W | 91546491 | Under construction | FALSE | [5 empty] | MS 11!V20
ZLM-0674 | MS 11 | K 11,3 | 1163 | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 11!G25
ZLM-0675 | MS 11 | K 11,3 | 1164 | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 11!G26
ZLM-0676 | MS 11 | K 11,3 | 1213 | Stand | 63A | R | 87819359 | Under construction | FALSE | [5 empty] | MS 11!G27
ZLM-0677 | MS 11 | K 11,3 | 1214 | Stand | 63A | R | 91546504 | Under construction | FALSE | [5 empty] | MS 11!G28
ZLM-0678 | MS 11 | K 11,3 | 1249 | Stand | 63A | B | 75091279 | Occupied | FALSE | [5 empty] | MS 11!G29
ZLM-0679 | MS 11 | K 11,1 | 1157 | Stand | 63A | B | 87819377 | Occupied | FALSE | [5 empty] | MS 11!Q25
ZLM-0680 | MS 11 | K 11,1 | 1159 | Stand | 63A | R | 90007826 | Occupied | FALSE | [5 empty] | MS 11!Q26
ZLM-0681 | MS 11 | K 11,1 | 1158 | Stand | 63A | W | 91546334 | Under construction | FALSE | [5 empty] | MS 11!Q27
ZLM-0682 | MS 11 | K 11,1 | 1253 | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 11!Q28
ZLM-0683 | MS 11 | K 11,1 | 1252 | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 11!Q29
ZLM-0684 | MS 11 | K 11,1 | 1160 | Stand | 80A | W | 90007841 | Occupied | FALSE | [5 empty] | MS 11!Q30
ZLM-0685 | MS 11 | K 11,9 | 1229 | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 11!V25
ZLM-0686 | MS 11 | K 11,9 | 1228 | Stand | 63A | R | 84040352 | Occupied | FALSE | [5 empty] | MS 11!V26
ZLM-0687 | MS 11 | K 11,9 | 1236 | Stand | 63A | B | 85354424 | Occupied | FALSE | [5 empty] | MS 11!V27
ZLM-0688 | MS 11 | K 11,9 | 1235 | Stand | 63A | B | 42324391 | Occupied | FALSE | [5 empty] | MS 11!V28
ZLM-0689 | MS 11 | K 11,6 | 1243 | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 11!L26
ZLM-0690 | MS 11 | K 11,6 | 1221 | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 11!L27
ZLM-0691 | MS 11 | K 11,6 | 1222 | Stand | 63A | W | 84340907 | Occupied | FALSE | [5 empty] | MS 11!L28
ZLM-0692 | MS 11 | K 11,6 | ??? | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 11!L29 | Placeholder slot
ZLM-0693 | MS 11 | K 11,6 | ??? | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 11!L30 | Placeholder slot
ZLM-0694 | MS 11 | K 11,10 | 1230 | Stand | 63A | R | 91732894 | Under construction | FALSE | [5 empty] | MS 11!V33
ZLM-0695 | MS 11 | K 11,10 | 1231 | Stand | 63A | W | 85354429 | Occupied | FALSE | [5 empty] | MS 11!V34
ZLM-0696 | MS 11 | K 11,10 | 1232 | Stand | 63A | B | 46884738 | Occupied | FALSE | [5 empty] | MS 11!V35
ZLM-0697 | MS 11 | K 11,10 | 1233 | Stand | 63A | R | 85354415 | Occupied | FALSE | [5 empty] | MS 11!V36
ZLM-0698 | MS 11 | K 11,10 | 1234 | Stand | 63A | B | 85354242 | Occupied | FALSE | [5 empty] | MS 11!V37
ZLM-0699 | MS 11 | K 11,7 | 1223 | Stand | 63A | R | 87778564 | Occupied | FALSE | [5 empty] | MS 11!L35
ZLM-0700 | MS 11 | K 11,7 | 1225 | Stand | 63A | W | 84340959 | Occupied | FALSE | [5 empty] | MS 11!L36
ZLM-0701 | MS 11 | K 11,7 | 1226 | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 11!L37
ZLM-0702 | MS 11 | K 11,7 | 1241 | Stand | 63A | R | 85354383 | Occupied | FALSE | [5 empty] | MS 11!L38
ZLM-0703 | MS 11 | K 11,7 | 1242 | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 11!L39
ZLM-0704 | MS 11 | MS LV board | Streetlights Kiosk | Common / other | 63A | RWB? | 47369736 | Occupied | FALSE | [5 empty] | MS 11!row 10
ZLM-0705 | MS 12 | K 12,5 | 1192 | Stand | 63A | R | 91546356 | Occupied | FALSE | [5 empty] | MS 12!G16
ZLM-0706 | MS 12 | K 12,5 | 1193 | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 12!G17
ZLM-0707 | MS 12 | K 12,5 | 1194 | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 12!G18
ZLM-0708 | MS 12 | K 12,5 | 1195 | Stand | 63A | R | 91733055 | Under construction | FALSE | [5 empty] | MS 12!G19
ZLM-0709 | MS 12 | K 12,11 | ??? | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 12!L16 | Placeholder slot
ZLM-0710 | MS 12 | K 12,11 | ??? | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 12!L17 | Placeholder slot
ZLM-0711 | MS 12 | K 12,11 | ??? | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 12!L18 | Placeholder slot
ZLM-0712 | MS 12 | K 12,11 | ??? | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 12!L19 | Placeholder slot
ZLM-0713 | MS 12 | K 12,1 | 1213 | Stand | 63A | B | 87819359 | Under construction | FALSE | [5 empty] | MS 12!Q16
ZLM-0714 | MS 12 | K 12,1 | 1165 | Stand | 80 | R | 85354367 | Occupied | FALSE | [5 empty] | MS 12!Q17
ZLM-0715 | MS 12 | K 12,1 | 1166 | Stand | 63A | W | 90007861 | Occupied | FALSE | [5 empty] | MS 12!Q18
ZLM-0716 | MS 12 | K 12,1 | ??? | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 12!Q19 | Placeholder slot
ZLM-0717 | MS 12 | K 12,8 | 1172 | Stand | 63A | W | 85354647 | Occupied | FALSE | [5 empty] | MS 12!V16
ZLM-0718 | MS 12 | K 12,8 | 1171 | Stand | 63A | W | 47369645 | Occupied | FALSE | [5 empty] | MS 12!V17
ZLM-0719 | MS 12 | K 12,8 | 1190 | Stand | 63A | B | 91733378 | Occupied | FALSE | [5 empty] | MS 12!V18
ZLM-0720 | MS 12 | K 12,8 | ??? | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 12!V19 | Placeholder slot
ZLM-0721 | MS 12 | K 12,6 | 1197 | Stand | 63A | W | 63182282 | Occupied | FALSE | [5 empty] | MS 12!G24
ZLM-0722 | MS 12 | K 12,6 | ??? | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 12!G25 | Placeholder slot
ZLM-0723 | MS 12 | K 12,6 | ??? | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 12!G26 | Placeholder slot
ZLM-0724 | MS 12 | K 12,6 | ??? | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 12!G27 | Placeholder slot
ZLM-0725 | MS 12 | K 12,12 | ??? | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 12!L24 | Placeholder slot
ZLM-0726 | MS 12 | K 12,12 | 1182 | Stand | 63A | W | 87778561 | Occupied | FALSE | [5 empty] | MS 12!L25
ZLM-0727 | MS 12 | K 12,12 | 1183 | Stand | 63A | B | 62627202 | Occupied | FALSE | [5 empty] | MS 12!L26
ZLM-0728 | MS 12 | K 12,12 | 1186 | Stand | 63A | R | 66599667 | Under construction | FALSE | [5 empty] | MS 12!L27
ZLM-0729 | MS 12 | K 12,2 | 1169 | Stand | 63A | W | 75091319 | Occupied | FALSE | [5 empty] | MS 12!Q24
ZLM-0730 | MS 12 | K 12,2 | ??? | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 12!Q25 | Placeholder slot
ZLM-0731 | MS 12 | K 12,2 | ??? | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 12!Q26 | Placeholder slot
ZLM-0732 | MS 12 | K 12,2 | ??? | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 12!Q27 | Placeholder slot
ZLM-0733 | MS 12 | K 12,9 | 1178 | Stand | 63A | W | 71204669 | Occupied | FALSE | [5 empty] | MS 12!V24
ZLM-0734 | MS 12 | K 12,9 | 1189 | Stand | 63A | B | 87819136 | Occupied | FALSE | [5 empty] | MS 12!V25
ZLM-0735 | MS 12 | K 12,9 | 1188 | Stand | 63A | R | 68054337 | Under construction | FALSE | [5 empty] | MS 12!V26
ZLM-0736 | MS 12 | K 12,9 | ??? | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 12!V27 | Placeholder slot
ZLM-0737 | MS 12 | K 12,7 | 1201 | Stand | 63A | W | 46886667 | Occupied | FALSE | [5 empty] | MS 12!G32
ZLM-0738 | MS 12 | K 12,7 | ??? | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 12!G33 | Placeholder slot
ZLM-0739 | MS 12 | K 12,7 | ??? | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 12!G34 | Placeholder slot
ZLM-0740 | MS 12 | K 12,7 | ??? | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 12!G35 | Placeholder slot
ZLM-0741 | MS 12 | K 12,3 | 1207 | Stand | 63A | R | 90007899 | Occupied | FALSE | [5 empty] | MS 12!Q32
ZLM-0742 | MS 12 | K 12,3 | 1208 | Stand | 63A | W | 87819439 | Occupied | FALSE | [5 empty] | MS 12!Q33
ZLM-0743 | MS 12 | K 12,3 | 1209 | Stand | 63A | B | 75091118 | Occupied | FALSE | [5 empty] | MS 12!Q34
ZLM-0744 | MS 12 | K 12,3 | 1211 | Stand | 63A | W | 87778306 | Occupied | FALSE | [5 empty] | MS 12!Q35
ZLM-0745 | MS 12 | K 12,10 | 1173 | Stand | 63A | R | 84039896 | Occupied | FALSE | [5 empty] | MS 12!V32
ZLM-0746 | MS 12 | K 12,10 | ??? | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 12!V33 | Placeholder slot
ZLM-0747 | MS 12 | K 12,10 | ??? | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 12!V34 | Placeholder slot
ZLM-0748 | MS 12 | K 12,10 | ??? | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 12!V35 | Placeholder slot
ZLM-0749 | MS 12 | K 12,4 | 1202 | Stand | 63A | R | 84039883 | Occupied | FALSE | [5 empty] | MS 12!Q40
ZLM-0750 | MS 12 | K 12,4 | 1206 | Stand | 63A | B | 87819316 | Occupied | FALSE | [5 empty] | MS 12!Q41
ZLM-0751 | MS 12 | K 12,4 | ??? | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 12!Q42 | Placeholder slot
ZLM-0752 | MS 12 | K 12,4 | ??? | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 12!Q43 | Placeholder slot
ZLM-0753 | MS 12 | MS LV board | Streetlights Kiosk | Common / other | 60A | RWB? | 67021420 | Occupied | FALSE | [5 empty] | MS 12!row 10
ZLM-0754 | MS 13 | K 13,7 | 1638 | Stand | 63A | R | 68053935 | Under construction | FALSE | [5 empty] | MS 13!G16
ZLM-0755 | MS 13 | K 13,7 | ??? | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 13!G17 | Placeholder slot
ZLM-0756 | MS 13 | K 13,7 | ??? | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 13!G18 | Placeholder slot
ZLM-0757 | MS 13 | K 13,7 | ??? | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 13!G19 | Placeholder slot
ZLM-0758 | MS 13 | K 13,8 | 1623 | Stand | 63A | B | 87819264 | Occupied | FALSE | [5 empty] | MS 13!L16
ZLM-0759 | MS 13 | K 13,8 | 1624 | Stand | 63A | B | 87778553 | Occupied | FALSE | [5 empty] | MS 13!L17
ZLM-0760 | MS 13 | K 13,8 | 1637 | Stand | 63A | R | 47369623 | Occupied | FALSE | [5 empty] | MS 13!L18
ZLM-0761 | MS 13 | K 13,8 | 1636 | Stand | 80A | RWB | 94991752 | Occupied | FALSE | [5 empty] | MS 13!L19
ZLM-0762 | MS 13 | K 13,4 | 1610 | Stand | 63A | W | 90007881 | Occupied | FALSE | [5 empty] | MS 13!Q16
ZLM-0763 | MS 13 | K 13,4 | 1609 | Stand | 63A | B | 87819363 | Occupied | FALSE | [5 empty] | MS 13!Q17
ZLM-0764 | MS 13 | K 13,4 | 1648 | Stand | 63A | R | 67020680 | Occupied | FALSE | [5 empty] | MS 13!Q18
ZLM-0765 | MS 13 | K 13,4 | 1649 | Stand | 63A | R | 91546042 | Occupied | FALSE | [5 empty] | MS 13!Q19
ZLM-0766 | MS 13 | K 13,4 | ??? | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 13!Q20 | Placeholder slot
ZLM-0767 | MS 13 | K 13,6 | 1615 | Stand | 63A | W | 87819231 | Occupied | FALSE | [5 empty] | MS 13!G24
ZLM-0768 | MS 13 | K 13,6 | 1642 | Stand | 63A | R | 90007903 | Occupied | FALSE | [5 empty] | MS 13!G25
ZLM-0769 | MS 13 | K 13,6 | 1643 | Stand | 63A | R | 90007965 | Occupied | FALSE | [5 empty] | MS 13!G26
ZLM-0770 | MS 13 | K 13,6 | ??? | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 13!G27 | Placeholder slot
ZLM-0771 | MS 13 | K 13,6 | ??? | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 13!G28 | Placeholder slot
ZLM-0772 | MS 13 | K 13,9 | 1635 | Stand | 63A | R | 46884462 | Under construction | FALSE | [5 empty] | MS 13!L24
ZLM-0773 | MS 13 | K 13,9 | 1634 | Stand | 80A | RWB | 98819663 | Under construction | FALSE | [5 empty] | MS 13!L25
ZLM-0774 | MS 13 | K 13,9 | 1625 | Stand | 63A | W | 85354230 | Under construction | FALSE | [5 empty] | MS 13!L26
ZLM-0775 | MS 13 | K 13,9 | ??? | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 13!L27 | Placeholder slot
ZLM-0776 | MS 13 | K 13,3 | 1608 | Stand | 63A | R | 77308344 | Occupied | FALSE | [5 empty] | MS 13!Q25
ZLM-0777 | MS 13 | K 13,3 | 1651 | Stand | 63A | B | 91733056 | Under construction | FALSE | [5 empty] | MS 13!Q26
ZLM-0778 | MS 13 | K 13,3 | ??? | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 13!Q27 | Placeholder slot
ZLM-0779 | MS 13 | K 13,3 | ??? | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 13!Q28 | Placeholder slot
ZLM-0780 | MS 13 | K 13,10 | 1627 | Stand | 63A | B | 91732553 | Under construction | FALSE | [5 empty] | MS 13!L32
ZLM-0781 | MS 13 | K 13,10 | ??? | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 13!L33 | Placeholder slot
ZLM-0782 | MS 13 | K 13,10 | ??? | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 13!L34 | Placeholder slot
ZLM-0783 | MS 13 | K 13,10 | ??? | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 13!L35 | Placeholder slot
ZLM-0784 | MS 13 | K 13,10 | ??? | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 13!L36 | Placeholder slot
ZLM-0785 | MS 13 | K 13,10 | ??? | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 13!L37 | Placeholder slot
ZLM-0786 | MS 13 | K 13,5 | 1611 | Stand | 80A | R | 77308365 | Occupied | FALSE | [5 empty] | MS 13!G33
ZLM-0787 | MS 13 | K 13,5 | 1645 | Stand | 63A | W | 91546470 | Occupied | FALSE | [5 empty] | MS 13!G34
ZLM-0788 | MS 13 | K 13,5 | 1647 | Stand | 63A | R | 64120460 | Occupied | FALSE | [5 empty] | MS 13!G35
ZLM-0789 | MS 13 | K 13,5 | ??? | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 13!G36 | Placeholder slot
ZLM-0790 | MS 13 | K 13,5 | ??? | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 13!G37 | Placeholder slot
ZLM-0791 | MS 13 | K 13,5 | ??? | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 13!G38 | Placeholder slot
ZLM-0792 | MS 13 | K 13,2 | 1652 | Stand | 63A | B | 87819410 | Occupied | FALSE | [5 empty] | MS 13!Q33
ZLM-0793 | MS 13 | K 13,2 | 1603 | Stand | 63A | W | 91732624 | Under construction | FALSE | [5 empty] | MS 13!Q34
ZLM-0794 | MS 13 | K 13,2 | 1604 | Stand | 63A | B | 91732976 | Under construction | FALSE | [5 empty] | MS 13!Q35
ZLM-0795 | MS 13 | K 13,2 | ??? | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 13!Q36 | Placeholder slot
ZLM-0796 | MS 13 | K 13,1 | 1601 | Stand | 63A | W | 85353994 | Occupied | FALSE | [5 empty] | MS 13!Q41
ZLM-0797 | MS 13 | K 13,1 | 1655 | Stand | 63A | RWB | 83014346 | Occupied | FALSE | [5 empty] | MS 13!Q42
ZLM-0798 | MS 13 | K 13,1 | 1654 | Stand | 63A | R | 91732563 | Under construction | FALSE | [5 empty] | MS 13!Q43
ZLM-0799 | MS 13 | K 13,1 | ??? | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 13!Q44 | Placeholder slot
ZLM-0800 | MS 13 | K 13,1 | ??? | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 13!Q45 | Placeholder slot
ZLM-0801 | MS 13 | K 13,11 | 1619 | Stand | 63A | R | 85354607 | Occupied | FALSE | [5 empty] | MS 13!G43
ZLM-0802 | MS 13 | K 13,11 | 1618 | Stand | 63A | W | 87819438 | Occupied | FALSE | [5 empty] | MS 13!G44
ZLM-0803 | MS 13 | K 13,11 | 1620 | Stand | 63A | B | 87819236 | Occupied | FALSE | [5 empty] | MS 13!G45
ZLM-0804 | MS 13 | K 13,11 | 1622 | Stand | 63A | W | 42607110 | Occupied | FALSE | [5 empty] | MS 13!G46
ZLM-0805 | MS 13 | K 13,11 | 1621 | Stand | 63A | R | 91546243 | Under construction | FALSE | [5 empty] | MS 13!G47
ZLM-0806 | MS 13 | K 13,11 | ??? | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 13!G48 | Placeholder slot
ZLM-0807 | MS 13 | MS LV board | Streetlights | Common / other | 60A | RWB? | 47369881 | Occupied | FALSE | [5 empty] | MS 13!row 10
ZLM-0808 | MS 14 | K 14,9 | 1661 | Stand | 63A | R | 85353973 | Occupied | FALSE | [5 empty] | MS 14!L16
ZLM-0809 | MS 14 | K 14,9 | 1662 | Stand | 63A | W | 90008041 | Occupied | FALSE | [5 empty] | MS 14!L17
ZLM-0810 | MS 14 | K 14,9 | 1705_03 | Stand | 63A | W | 46884021 | Occupied | FALSE | [5 empty] | MS 14!L18
ZLM-0811 | MS 14 | K 14,9 | 1660 | Stand | 63A | R | 91546248 | Under construction | FALSE | [5 empty] | MS 14!L19
ZLM-0812 | MS 14 | K 14,9 | ??? | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 14!L20 | Placeholder slot
ZLM-0813 | MS 14 | K 14,9 | ??? | Stand | - | - |  | Vacant | FALSE | [5 empty] | MS 14!L21 | Placeholder slot
ZLM-0814 | MS 14 | K 14,5 | 1580 | Stand | 63A | W | 90008067 | Occupied | FALSE | [5 empty] | MS 14!Q16
ZLM-0815 | MS 14 | K 14,5 | 1579 | Stand | 63A | R | 91733082 | Under construction | FALSE | [5 empty] | MS 14!Q17
ZLM-0816 | MS 14 | K 14,5 | ??? | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 14!Q18 | Placeholder slot
ZLM-0817 | MS 14 | K 14,5 | ??? | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 14!Q19 | Placeholder slot
ZLM-0818 | MS 14 | K 14,2 | 1674 | Stand | 63A | B | 85354375 | Occupied | FALSE | [5 empty] | MS 14!V16
ZLM-0819 | MS 14 | K 14,2 | ??? | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 14!V17 | Placeholder slot
ZLM-0820 | MS 14 | K 14,2 | ??? | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 14!V18 | Placeholder slot
ZLM-0821 | MS 14 | K 14,2 | ??? | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 14!V19 | Placeholder slot
ZLM-0822 | MS 14 | K 14,2 | ??? | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 14!V20 | Placeholder slot
ZLM-0823 | MS 14 | K 14,9 A | 1705-04 | Stand | 63A | B | 67020973 | Occupied | FALSE | [5 empty] | MS 14!G20
ZLM-0824 | MS 14 | K 14,9 A | 1705-01 | Stand | 63A | R | 91546309 | Occupied | FALSE | [5 empty] | MS 14!G21
ZLM-0825 | MS 14 | K 14,9 A | 1705-02 | Stand | 63A | W | 91733103 | Occupied | FALSE | [5 empty] | MS 14!G22
ZLM-0826 | MS 14 | K 14,9 A | 1705-06 | Stand | 63A | R | 91732997 | Occupied | FALSE | [5 empty] | MS 14!G23
ZLM-0827 | MS 14 | K 14,9 A | 1705-05 | Stand | 63A | B | 91546211 | Under construction | FALSE | [5 empty] | MS 14!G24
ZLM-0828 | MS 14 | K 14,4 | 1577 | Stand | 63A | W | 90007925 | Occupied | FALSE | [5 empty] | MS 14!Q24
ZLM-0829 | MS 14 | K 14,4 | 1666 | Stand | 63A | R | 91733375 | Occupied | FALSE | [5 empty] | MS 14!Q25
ZLM-0830 | MS 14 | K 14,4 | 1573 | Stand | 63A | B | 91732540 | Under construction | FALSE | [5 empty] | MS 14!Q26
ZLM-0831 | MS 14 | K 14,4 | 1575 | Stand | 63A | R | 90007912 | Occupied | FALSE | [5 empty] | MS 14!Q27
ZLM-0832 | MS 14 | K 14,4 | ??? | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 14!Q28 | Placeholder slot
ZLM-0833 | MS 14 | K 14,4 | ??? | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 14!Q29 | Placeholder slot
ZLM-0834 | MS 14 | K 14,1 | 1675 | Stand | 63A | B | 91732616 | Occupied | FALSE | [5 empty] | MS 14!V25
ZLM-0835 | MS 14 | K 14,1 | 1680 | Stand | 63A | R | 91733385 | Under construction | FALSE | [5 empty] | MS 14!V26
ZLM-0836 | MS 14 | K 14,1 | 1679 | Stand | 63A | B | 90007864 | Occupied | FALSE | [5 empty] | MS 14!V27
ZLM-0837 | MS 14 | K 14,1 | ??? | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 14!V28 | Placeholder slot
ZLM-0838 | MS 14 | K 14,1 | ??? | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 14!V29 | Placeholder slot
ZLM-0839 | MS 14 | K 14,10 | 1658 | Stand | 63A | B | 91073494 | Occupied | FALSE | [5 empty] | MS 14!L28
ZLM-0840 | MS 14 | K 14,10 | 1659 | Stand | 63A | R | 91546494 | Under construction | FALSE | [5 empty] | MS 14!L29
ZLM-0841 | MS 14 | K 14,10 | ??? | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 14!L30 | Placeholder slot
ZLM-0842 | MS 14 | K 14,10 | ??? | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 14!L31 | Placeholder slot
ZLM-0843 | MS 14 | K 14,10 | ??? | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 14!L32 | Placeholder slot
ZLM-0844 | MS 14 | K 14,9 B | 1705 DEV | Stand | 63A | R | 91733069 | Under construction | FALSE | [5 empty] | MS 14!G29
ZLM-0845 | MS 14 | K 14,9 B | - | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 14!G30 | Placeholder slot
ZLM-0846 | MS 14 | K 14,9 B | - | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 14!G31 | Placeholder slot
ZLM-0847 | MS 14 | K 14,9 B | - | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 14!G32 | Placeholder slot
ZLM-0848 | MS 14 | K 14,3 | 1572 | Stand | 63A | W | 47369883 | Occupied | FALSE | [5 empty] | MS 14!Q34
ZLM-0849 | MS 14 | K 14,3 | 1667 | Stand | 80A | RWB | 94992077 | Occupied | FALSE | [5 empty] | MS 14!Q35
ZLM-0850 | MS 14 | K 14,3 | ??? | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 14!Q36 | Placeholder slot
ZLM-0851 | MS 14 | K 14,3 | ??? | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 14!Q37 | Placeholder slot
ZLM-0852 | MS 14 | K 14,10 A | 1705-18 | Stand | 63A | W | 91546219 | Under construction | FALSE | [5 empty] | MS 14!G38
ZLM-0853 | MS 14 | K 14,10 A | - | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 14!G39 | Placeholder slot
ZLM-0854 | MS 14 | K 14,10 A | - | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 14!G40 | Placeholder slot
ZLM-0855 | MS 14 | K 14,10 A | - | Stand | 63A | - |  | Vacant | FALSE | [5 empty] | MS 14!G41 | Placeholder slot
ZLM-0856 | MS 14 | K 14,11 | 1656 | Stand | 63A | B | 90008070 | Occupied | FALSE | [5 empty] | MS 14!L38
ZLM-0857 | MS 14 | K 14,11 | 1705_20 | Stand | 63A | W | 90008093 | Occupied | FALSE | [5 empty] | MS 14!L39
ZLM-0858 | MS 14 | K 14,11 | 1657 | Stand | 63A | R | 91732517 | Under construction | FALSE | [5 empty] | MS 14!L40
ZLM-0859 | MS 14 | K 14,11 | 1600 | Stand | 63A | W | 91733001 | Under construction | FALSE | [5 empty] | MS 14!L41
ZLM-0860 | MS 14 | MS LV board | Streetlights | Common / other | 63A | RWB? | 42866655 | Occupied | FALSE | [5 empty] | MS 14!row 10
ZLM-0861 | MS 02 | 511 Husk Meter Panel 2 | 511-11 | Stand |  |  | 90007868 | Occupied | TRUE | 2cf7f120526050b8 | 1 | ZLM 511-11 [Husk] | 10/4/2026, 07:55 AM |  | AMR export 05 Oct 2026 | Added from AMR export – not in reticulation sheet
ZLM-0862 | MS 02 | 511 Husk Meter Panel 2 | 511-12 | Stand |  |  | 90007860 | Occupied | TRUE | 2cf7f120526050b8 | 2 | ZLM 511-12 [Husk] | 10/4/2026, 07:55 AM |  | AMR export 05 Oct 2026 | Added from AMR export – not in reticulation sheet
ZLM-0863 | MS 02 | 511 Husk Meter Panel 2 | 511-13 | Stand |  |  | 90007940 | Occupied | TRUE | 2cf7f120526050b8 | 3 | ZLM 511-13 [Husk] | 10/4/2026, 07:55 AM |  | AMR export 05 Oct 2026 | Added from AMR export – not in reticulation sheet
ZLM-0864 | MS 02 | 511 Husk Meter Panel 2 | 511-14 | Stand |  |  | 90007896 | Occupied | TRUE | 2cf7f120526050b8 | 4 | ZLM 511-14 [Husk] | 10/4/2026, 07:55 AM |  | AMR export 05 Oct 2026 | Added from AMR export – not in reticulation sheet
ZLM-0865 | MS 02 | 511 Husk Meter Panel 2 | 511-15 | Stand |  |  | 90007850 | Occupied | TRUE | 2cf7f120526050b8 | 5 | ZLM 511-15 [Husk] | 10/4/2026, 07:55 AM |  | AMR export 05 Oct 2026 | Added from AMR export – not in reticulation sheet
ZLM-0866 | MS 02 | 511 Husk Meter Panel 2 | 511-16 | Stand |  |  |  | Occupied | TRUE | 2cf7f120526050b8 | 6 | ZLM 511-16 [Husk] - meter removed | 7/20/2026, 04:59 PM |  | AMR export 05 Oct 2026 | Meter removed – AMR channel still registered
ZLM-0867 | MS 02 | 511 Husk Meter Panel 2 | 511-17 | Stand |  |  | 90007812 | Occupied | TRUE | 2cf7f120526050b8 | 7 | ZLM 511-17 [Husk] | 10/4/2026, 07:55 AM |  | AMR export 05 Oct 2026 | Added from AMR export – not in reticulation sheet
ZLM-0868 | MS 02 | 511 Husk Meter Panel 2 | 511-18 | Stand |  |  | 90007872 | Occupied | TRUE | 2cf7f120526050b8 | 8 | ZLM 511-18 [Husk] | 10/4/2026, 07:55 AM |  | AMR export 05 Oct 2026 | Added from AMR export – not in reticulation sheet
ZLM-0869 | MS 02 | 511 Husk Meter Panel 2 | 511-19 | Stand |  |  | 90007835 | Occupied | TRUE | 2cf7f120526050b8 | 9 | ZLM 511-19 [Husk] | 10/5/2026, 08:25 AM |  | AMR export 05 Oct 2026 | Added from AMR export – not in reticulation sheet
ZLM-0870 | MS 02 | 511 Husk Meter Panel 2 | 511-20 | Stand |  |  | 90007888 | Occupied | TRUE | 2cf7f120526050b8 | 10 | ZLM 511-20 [Husk] | 10/5/2026, 08:25 AM |  | AMR export 05 Oct 2026 | Added from AMR export – not in reticulation sheet
ZLM-0871 | MS 02 | 511 Husk Meter Panel 2 | 511-21 | Stand |  |  | 90007851 | Occupied | TRUE | 2cf7f120526050b8 | 11 | ZLM 511-21 [Husk] | 10/5/2026, 08:25 AM |  | AMR export 05 Oct 2026 | Added from AMR export – not in reticulation sheet
ZLM-0872 | MS 02 | 511 Husk Meter Panel 2 | 511-22 | Stand |  |  | 90007936 | Occupied | TRUE | 2cf7f120526050b8 | 12 | ZLM 511-22 [Husk] | 10/5/2026, 08:25 AM |  | AMR export 05 Oct 2026 | Added from AMR export – not in reticulation sheet
ZLM-0873 | MS 02 | 511 Husk Meter Panel 2 | 511-23 | Stand |  |  | 90007818 | Occupied | TRUE | 2cf7f120526050b8 | 13 | ZLM 511-23 [Husk] | 10/5/2026, 08:25 AM |  | AMR export 05 Oct 2026 | Added from AMR export – not in reticulation sheet
ZLM-0874 | MS 02 | 511 Husk Meter Panel 2 | 511-24 | Stand |  |  | 90007916 | Occupied | TRUE | 2cf7f120526050b8 | 14 | ZLM 511-24 [Husk] | 10/5/2026, 08:25 AM |  | AMR export 05 Oct 2026 | Added from AMR export – not in reticulation sheet
ZLM-0875 | MS 02 | 511 Husk Meter Panel 1 | 511-01 | Stand |  |  | 90007819 | Occupied | TRUE | 2cf7f120526010ac | 1 | ZLM 511-01 Husk | 10/3/2026, 09:34 PM |  | AMR export 05 Oct 2026 | Added from AMR export – not in reticulation sheet
ZLM-0876 | MS 02 | 511 Husk Meter Panel 1 | 511-02 | Stand |  |  | 90007884 | Occupied | TRUE | 2cf7f120526010ac | 2 | ZLM 511-02 Husk | 10/3/2026, 09:34 PM |  | AMR export 05 Oct 2026 | Added from AMR export – not in reticulation sheet
ZLM-0877 | MS 02 | 511 Husk Meter Panel 1 | 511-03 | Stand |  |  | 90007836 | Occupied | TRUE | 2cf7f120526010ac | 3 | ZLM 511-03 Husk | 10/3/2026, 09:34 PM |  | AMR export 05 Oct 2026 | Added from AMR export – not in reticulation sheet
ZLM-0878 | MS 02 | 511 Husk Meter Panel 1 | 511-04 | Stand |  |  | 90007908 | Occupied | TRUE | 2cf7f120526010ac | 4 | ZLM 511-04 Husk | 10/3/2026, 09:34 PM |  | AMR export 05 Oct 2026 | Added from AMR export – not in reticulation sheet
ZLM-0879 | MS 02 | 511 Husk Meter Panel 1 | 511-05 | Stand |  |  | 90007843 | Occupied | TRUE | 2cf7f120526010ac | 5 | ZLM 511-05 Husk | 10/3/2026, 09:34 PM |  | AMR export 05 Oct 2026 | Added from AMR export – not in reticulation sheet
ZLM-0880 | MS 02 | 511 Husk Meter Panel 1 | 511-06 | Stand |  |  | 90007900 | Occupied | TRUE | 2cf7f120526010ac | 6 | ZLM 511-06 Husk | 10/3/2026, 09:34 PM |  | AMR export 05 Oct 2026 | Added from AMR export – not in reticulation sheet
ZLM-0881 | MS 02 | 511 Husk Meter Panel 1 | 511-07 | Stand |  |  | 90007840 | Occupied | TRUE | 2cf7f120526010ac | 7 | ZLM 511-07 Husk | 10/3/2026, 09:34 PM |  | AMR export 05 Oct 2026 | Added from AMR export – not in reticulation sheet
ZLM-0882 | MS 02 | 511 Husk Meter Panel 1 | 511-08 | Stand |  |  | 90007817 | Occupied | TRUE | 2cf7f120526010ac | 8 | ZLM 511-08 Husk | 10/3/2026, 09:34 PM |  | AMR export 05 Oct 2026 | Added from AMR export – not in reticulation sheet
ZLM-0883 | MS 02 | 511 Husk Meter Panel 1 | 511-09 | Stand |  |  | 90007806 | Occupied | TRUE | 2cf7f120526010ac | 9 | ZLM 511-09 Husk | 10/4/2026, 09:59 PM |  | AMR export 05 Oct 2026 | Added from AMR export – not in reticulation sheet
ZLM-0884 | MS 02 | 511 Husk Meter Panel 1 | 511-10 | Stand |  |  | 90007808 | Occupied | TRUE | 2cf7f120526010ac | 10 | ZLM 511-10 Husk | 10/4/2026, 09:59 PM |  | AMR export 05 Oct 2026 | Added from AMR export – not in reticulation sheet

## Kiosks
Minisub | Kiosk | Kiosk Type | Fed From | Feed Breaker / Cable | Feed Link Basis | Kiosk Main Breaker | Next Kiosk Supply | Supplies | Planned AMR Unit | AMR Device(s) | AMR Order | AMR Status | KMZ Point | Latitude | Longitude | Source
MS 01 | MS LV board | MS LV board (direct supplies) | [5 empty] | 3 | 8-probe |  |  | Outstanding | MS 01 | -29.4825 | 31.2501 | MS 01 row 8–10
MS 01 | 505 Aura K08 | Metering kiosk | 505 Aura K03 | 250A | Feeder row in kiosk (sheet) | 250A | 250A | 6 | 8-probe |  |  | Outstanding |  |  |  | MS 01!Q38
MS 01 | 505 Aura K09 | Metering kiosk | 505 Aura K08 | 250A | Inferred from sheet layout | 160A | ???A | 4 | 8-probe |  |  | Outstanding |  |  |  | MS 01!Q48
MS 01 | 505 Aura K10 | Metering kiosk | 505 Aura K09 |  | Inferred from sheet layout | 100A | ???A | 4 | 8-probe |  |  | Outstanding |  |  |  | MS 01!Q56
MS 01 | 505 Aura K11 | Metering kiosk | 505 Aura K10 |  | Inferred from sheet layout | 125A | ???A | 4 | 8-probe |  |  | Outstanding |  |  |  | MS 01!Q64
MS 01 | 505 Aura K12 | Metering kiosk | 505 Aura K11 |  | Inferred from sheet layout | 125A | NA | 4 | 8-probe |  |  | Outstanding |  |  |  | MS 01!Q72
MS 01 | 505 Aura K01 | Metering kiosk | MS LV board | 250A | MS LV board (sheet) | 200A | 250A | 4 | 8-probe |  |  | Outstanding |  |  |  | MS 01!V13
MS 01 | 505 Aura K02 | Metering kiosk | 505 Aura K01 | 250A | Inferred from sheet layout | 250A | 250A | 4 | 8-probe |  |  | Outstanding |  |  |  | MS 01!V21
MS 01 | 505 Aura K03 | Metering kiosk | 505 Aura K02 | 250A | Inferred from sheet layout | 250A | 200A | 4 | 8-probe |  |  | Outstanding |  |  |  | MS 01!V29
MS 01 | 505 Aura K04 | Metering kiosk | 505 Aura K03 | 200A | Inferred from sheet layout | 100A | ???A | 5 | 8-probe |  |  | Outstanding |  |  |  | MS 01!V38
MS 01 | 505 Aura K05 | Metering kiosk | 505 Aura K04 |  | Inferred from sheet layout | 100A | ???A | 4 | 8-probe |  |  | Outstanding |  |  |  | MS 01!V47
MS 01 | 505 Aura K06 | Metering kiosk | 505 Aura K05 |  | Inferred from sheet layout | 125A | ???A | 4 | 8-probe |  |  | Outstanding |  |  |  | MS 01!V55
MS 01 | 505 Aura K07 | Metering kiosk | 505 Aura K06 |  | Inferred from sheet layout | 125A | NA | 4 | 8-probe |  |  | Outstanding |  |  |  | MS 01!V63
MS 02 | MS LV board | MS LV board (direct supplies) | [5 empty] | 1 | Standalone |  |  | Outstanding | MS 02 | -29.4821 | 31.2522 | MS 02 row 8–10
MS 02 | K 2,1 | Metering kiosk | MS LV board | 200A | MS LV board (sheet) | 250A | ???A | 6 | 8-probe |  |  | Outstanding | K 2.1 | -29.482 | 31.2529 | MS 02!G13
MS 02 | 513 Azure LV Kiosk | Metering kiosk | MS LV board | 250A | MS LV board (sheet) | 150A | ???A | 1 | Standalone |  |  | Outstanding | 513 Azure - LV Kiosk | -29.4825 | 31.2515 | MS 02!Q13
MS 02 | 513 K 1,1 | Metering kiosk | 513 Azure LV Kiosk | 100A | Feeder row in kiosk (sheet) | 100A | ???A | 2 | 8-probe |  |  | Outstanding |  |  |  | MS 02!Q23
MS 02 | 513 K 1,2 | Metering kiosk | 513 K 1,1 |  | Inferred from sheet layout | 100A | ???A | 4 | 8-probe |  |  | Outstanding |  |  |  | MS 02!Q29
MS 02 | 513 K 1,3 | Metering kiosk | 513 K 1,2 |  | Inferred from sheet layout | 63A | ???A | 3 | 8-probe |  |  | Outstanding |  |  |  | MS 02!Q37
MS 02 | 513 K 1,4 | Metering kiosk | 513 Azure LV Kiosk | 80A | Feeder row in kiosk (sheet) | 150A | ???A | 3 | 8-probe |  |  | Outstanding |  |  |  | MS 02!Q44
MS 02 | 513 K 1,5 | Metering kiosk | 513 K 1,4 |  | Inferred from sheet layout | 150A | NA | 4 | 8-probe |  |  | Outstanding |  |  |  | MS 02!Q51
MS 02 | 512 Kiosk 1 | Metering kiosk | MS LV board | 200A | MS LV board (sheet) | 250A | ???A | 3 | 8-probe |  |  | Outstanding |  |  |  | MS 02!V13
MS 02 | 512 Kiosk 2 | Metering kiosk | 512 Kiosk 1 | 200A (95mm) | Feeder row in kiosk (sheet) | 160A | ???A | 3 | 8-probe |  |  | Outstanding |  |  |  | MS 02!V21
MS 02 | 512 Kiosk 3 | Metering kiosk | 512 Kiosk 2 | 100A | Feeder row in kiosk (sheet) | ???A ( * 4) |  | 2 | 8-probe |  |  | Outstanding |  |  |  | MS 02!V30
MS 02 | 512 Kiosk 4 | Metering kiosk | 512 Kiosk 2 | 100A (95mm) | Feeder row in kiosk (sheet) | 160A | ???A | 3 | 8-probe |  |  | Outstanding |  |  |  | MS 02!V38
MS 02 | 512 Kiosk 5 | Metering kiosk | 512 Kiosk 4 | 160A (70mm) | Feeder row in kiosk (sheet) | 160A | ???A | 3 | 8-probe |  |  | Outstanding |  |  |  | MS 02!V46
MS 02 | 512 Kiosk 6 | Metering kiosk | 512 Kiosk 5 | 160A (70mm) | Feeder row in kiosk (sheet) | ???A ( * 4) |  | 2 | 8-probe |  |  | Outstanding |  |  |  | MS 02!V54
MS 02 | 511 Husk Meter Panel 2 | Meter panel | 511 Husk Meter Panel 1 |  | Assumed (not in sheet) |  |  | 14 | 16-probe | 2cf7f120526050b8 |  | Installed | 511 Husk - Meter panel 2 | -29.4835 | 31.253 | AMR export
MS 02 | 511 Husk Meter Panel 1 | Meter panel | MS LV board | 200A | MS LV board (sheet) |  |  | 10 | 16-probe | 2cf7f120526010ac |  | Installed | 511 Husk - Meter panel 1 | -29.4832 | 31.2533 | AMR export
MS 03 | MS LV board | MS LV board (direct supplies) | [5 empty] | 1 | Standalone |  |  | Outstanding | MS 03 | -29.4811 | 31.2491 | MS 03 row 8–10
MS 03 | K 3,1 | Metering kiosk | MS LV board | 60A | MS LV board (sheet) | 63A | NA | 4 | 8-probe |  |  | Outstanding | K 3.1 | -29.4806 | 31.2497 | MS 03!G13
MS 03 | K 2,1 | Metering kiosk | MS LV board | 80A | MS LV board (sheet) | 80A | ???A | 5 | 8-probe |  |  | Outstanding | K2.1 | -29.4803 | 31.2504 | MS 03!L13
MS 03 | K 2,2 | Metering kiosk | K 2,1 |  | Inferred from sheet layout | 63A | NA | 4 | 8-probe |  |  | Outstanding | K 2.2 | -29.4806 | 31.25 | MS 03!L22
MS 03 | K 3,2 | Metering kiosk | MS LV board | 100A | MS LV board (sheet) | 125A | NA | 4 | 8-probe |  |  | Outstanding | K 3.2 | -29.4811 | 31.249 | MS 03!Q13
MS 03 | K 3,3 | Metering kiosk | ? |  | Unconfirmed – not referenced in sheet | 80A | NA | 6 | 8-probe |  |  | Outstanding | K 3.3 | -29.4816 | 31.2488 | MS 03!Q21
MS 03 | K 3,4 | Metering kiosk | MS LV board | 100A | MS LV board (sheet) | 80A | ???A | 4 | 8-probe |  |  | Outstanding | K 3.4 | -29.4819 | 31.2485 | MS 03!V13
MS 03 | K 3,5 | Metering kiosk | K 3,4 |  | Inferred from sheet layout | 50A | ???A | 4 | 8-probe |  |  | Outstanding | K 3.5 | -29.4821 | 31.2483 | MS 03!V21
MS 03 | K 3,10 | Metering kiosk | K 3,5 |  | Inferred from sheet layout | 50A | NA | 4 | 8-probe |  |  | Outstanding | K3.10 | -29.4819 | 31.249 | MS 03!V29
MS 03 | K 2,3 | Metering kiosk | MS LV board | 125A | MS LV board (sheet) | 125A | ???A | 4 | 8-probe |  |  | Outstanding | K 2.3 | -29.4809 | 31.2495 | MS 03!AA13
MS 03 | K 2,4 | Metering kiosk | K 2,3 |  | Inferred from sheet layout | 100A | NA | 4 | 8-probe |  |  | Outstanding | K 2.4 | -29.4812 | 31.2496 | MS 03!AA21
MS 03 | 1707 LV | Metering kiosk | MS LV board | 400A | MS LV board (sheet) | 400A | NA | 1 | Standalone |  |  | Outstanding |  |  |  | MS 03!AF13
MS 03 | 1707 K 3,10 | Metering kiosk | 1707 LV | 80A | Feeder row in kiosk (sheet) | 50A | NA | 3 | 8-probe |  |  | Outstanding |  |  |  | MS 03!AF21
MS 03 | 1707 K 3,7 | Metering kiosk | 1707 LV | 200A | Feeder row in kiosk (sheet) | 200A | 150A | 14 | 16-probe |  |  | Outstanding |  |  |  | MS 03!AK17
MS 03 | 1707 K 3,8 | Metering kiosk | 1707 K 3,7 | 150A | Inferred from sheet layout | 150A | 80A | 10 | 16-probe |  |  | Outstanding |  |  |  | MS 03!AK35
MS 03 | 1707 K 3,9 | Metering kiosk | 1707 K 3,8 | 80A | Inferred from sheet layout | 80A | NA | 10 | 16-probe |  |  | Outstanding |  |  |  | MS 03!AK49
MS 03 | 1707 K 3,4 | Metering kiosk | 1707 LV | 200A | Feeder row in kiosk (sheet) | 200A | 150A | 7 | 8-probe |  |  | Outstanding |  |  |  | MS 03!AP17
MS 03 | 1707 K 3,5 | Metering kiosk | 1707 K 3,4 | 150A | Inferred from sheet layout | 200A | 150A | 7 | 8-probe |  |  | Outstanding |  |  |  | MS 03!AP28
MS 03 | 1707 K 3,6 | Metering kiosk | 1707 K 3,5 | 150A | Inferred from sheet layout | 80A | NA | 10 | 16-probe |  |  | Outstanding |  |  |  | MS 03!AP39
MS 04 | K 1,1 | Metering kiosk | MS LV board | 120A | MS LV board (sheet) | 125A | 100A | 5 | 8-probe |  |  | Outstanding | K 1.1 | -29.4741 | 31.2505 | MS 04 - Coral!B13
MS 04 | K 1,2 | Metering kiosk | K 1,1 | 100A | Inferred from sheet layout | 125A | 80A | 6 | 8-probe |  |  | Outstanding | K 1.2 | -29.4734 | 31.2507 | MS 04 - Coral!B22
MS 04 | K 1,3 | Metering kiosk | K 1,2 | 80A | Inferred from sheet layout | 125A | 60A | 6 | 8-probe |  |  | Outstanding | K 1.3 | -29.4727 | 31.2513 | MS 04 - Coral!B32
MS 04 | K 1,8 | Metering kiosk | K 1,3 | 60A | Inferred from sheet layout | 63A | 60A | 4 | 8-probe |  |  | Outstanding | K 1.8 | -29.4726 | 31.2503 | MS 04 - Coral!B42
MS 04 | K 1,9 | Metering kiosk | K 1,8 | 60A | Inferred from sheet layout | 63A | 40A | 5 | 8-probe |  |  | Outstanding | K 1.9 | -29.4721 | 31.2513 | MS 04 - Coral!B50
MS 04 | K G/H | Metering kiosk | K 1,9 | 40A | Inferred from sheet layout | 63A | NA | 1 | Standalone |  |  | Outstanding | K G/H | -29.4719 | 31.2518 | MS 04 - Coral!B59
MS 04 | K 1,4 | Metering kiosk | MS LV board | 120A | MS LV board (sheet) | 125A | 120A | 8 | 8-probe |  |  | Outstanding | K 1.4 | -29.4737 | 31.2509 | MS 04 - Coral!G13
MS 04 | K 1,6 | Metering kiosk | K 1,4 | 120A | Inferred from sheet layout | 125A | 60A | 9 | 16-probe |  |  | Outstanding | K 1.6 | -29.4732 | 31.2513 | MS 04 - Coral!G25
MS 04 | K 1,7 | Metering kiosk | K 1,6 | 60A | Inferred from sheet layout | 60A | NA | 6 | 8-probe |  |  | Outstanding | K 1.7 | -29.4728 | 31.2516 | MS 04 - Coral!G38
MS 04 | K 1,10 | Metering kiosk | MS LV board | 250A | MS LV board (sheet) | 250A | 200A | 7 | 8-probe |  |  | Outstanding | K1.10 | -29.4746 | 31.2502 | MS 04 - Coral!L13
MS 04 | K 1,11 | Metering kiosk | K 1,10 | 200A | Inferred from sheet layout | 200A | 100A | 9 | 16-probe |  |  | Outstanding | K 1.11 | -29.4752 | 31.2499 | MS 04 - Coral!L24
MS 04 | K 1,15 | Metering kiosk | K 1,11 | 100A | Inferred from sheet layout | 125A | 80A | 5 | 8-probe |  |  | Outstanding | K 1.15 | -29.4751 | 31.2494 | MS 04 - Coral!L38
MS 04 | K 1,16 | Metering kiosk | K 1,15 | 80A | Inferred from sheet layout | 63A | 60A | 6 | 8-probe |  |  | Outstanding | K 1.16 | -29.4755 | 31.2489 | MS 04 - Coral!L47
MS 04 | K 1,17 | Metering kiosk | K 1,16 | 60A | Inferred from sheet layout | 60A | NA | 6 | 8-probe |  |  | Outstanding | K 1.17 | -29.4764 | 31.2487 | MS 04 - Coral!L57
MS 04 | K 1,12 | Metering kiosk | K 1,11 | 120A | Feeder row in kiosk (sheet) | 125A | 80A | 4 | 8-probe |  |  | Outstanding | K 1.12 | -29.4757 | 31.2496 | MS 04 - Coral!Q38
MS 04 | K 1,13 | Metering kiosk | K 1,12 | 80A | Inferred from sheet layout | 125A | 60A | 9 | 16-probe |  |  | Outstanding | K 1.13 | -29.4761 | 31.2493 | MS 04 - Coral!Q46
MS 04 | K 1,14 | Metering kiosk | K 1,13 | 60A | Inferred from sheet layout | 63A | NA | 7 | 8-probe |  |  | Outstanding | K 1.14 | -29.4766 | 31.249 | MS 04 - Coral!Q59
MS 05 | MS LV board | MS LV board (direct supplies) | [5 empty] | 1 | Standalone |  |  | Outstanding | MS 05 | -29.4736 | 31.248 | MS 05 row 8–10
MS 05 | K 2,5 | Metering kiosk | MS LV board | 200A | MS LV board (sheet) | 250A | 120A | 9 | 16-probe |  |  | Outstanding | K 2.5 | -29.474 | 31.2477 | MS 05 - Coral!G13
MS 05 | K 2,6 | Metering kiosk | K 2,5 | 120A | Inferred from sheet layout | 120A | 100A | 7 | 8-probe |  |  | Outstanding | K 2.6 | -29.4744 | 31.2474 | MS 05 - Coral!G26
MS 05 | K 2,7 | Metering kiosk | K 2,6 | 100A | Inferred from sheet layout | 100A | 60A | 9 | 16-probe |  |  | Outstanding |  |  |  | MS 05 - Coral!G37
MS 05 | K 2,8 | Metering kiosk | K 2,7 | 60A | Inferred from sheet layout | 60A | NA | 9 | 16-probe |  |  | Outstanding |  |  |  | MS 05 - Coral!G50
MS 05 | K 2,9 | Metering kiosk | MS LV board | 250A | MS LV board (sheet) | 250A | 250A | 6 | 8-probe |  |  | Outstanding | K 2.9 | -29.4744 | 31.2483 | MS 05 - Coral!L13
MS 05 | K 2,14 | Metering kiosk | K 2,9 | 250A | Inferred from sheet layout | 250A | 200A | 3 | 8-probe |  |  | Outstanding | K 2.14 | -29.4748 | 31.2482 | MS 05 - Coral!L23
MS 05 | K 2,15 | Metering kiosk | K 2,14 | 200A | Inferred from sheet layout | 250A | 200A | 5 | 8-probe |  |  | Outstanding | K 2.15 | -29.4756 | 31.2478 | MS 05 - Coral!L30
MS 05 | K 2,16 | Metering kiosk | K 2,15 | 200A | Inferred from sheet layout | 250A | NA | 4 | 8-probe |  |  | Outstanding | K 2.16 | -29.4762 | 31.2475 | MS 05 - Coral!L39
MS 05 | K 2,19 | Metering kiosk | K 2,16 | 60A · 95mm | Feeder row in kiosk (sheet) | 60A | NA | 4 | 8-probe |  |  | Outstanding | K 2.19 | -29.477 | 31.2474 | MS 05 - Coral!L49
MS 05 | K 2,17 | Metering kiosk | K 2,16 | 100A · 95mm | Feeder row in kiosk (sheet) | 125A | NA | 5 | 8-probe |  |  | Outstanding | K 2.17 | -29.4765 | 31.247 | MS 05 - Coral!L57
MS 05 | K 2,18 | Metering kiosk | K 2,17 | 60A · 95mm | Feeder row in kiosk (sheet) | 60A | NA | 8 | 8-probe |  |  | Outstanding |  |  |  | MS 05 - Coral!L68
MS 05 | K 2,20 | Metering kiosk | K 2,17 | 60A · 95mm | Feeder row in kiosk (sheet) | 60A | NA | 5 | 8-probe |  |  | Outstanding | K 2.20 | -29.4768 | 31.247 | MS 05 - Coral!L80
MS 05 | K 2,10 | Metering kiosk | MS LV board | 200A | MS LV board (sheet) | 250A | NA | 7 | 8-probe |  |  | Outstanding | K 2.10 | -29.4749 | 31.2477 | MS 05 - Coral!Q13
MS 05 | K 2,11A | Metering kiosk | K 2,10 | 60A · 50mm | Feeder row in kiosk (sheet) | 60A | NA | 7 | 8-probe |  |  | Outstanding |  |  |  | MS 05 - Coral!Q26
MS 05 | K 2,11 | Metering kiosk | K 2,10 | 100A · 95mm | Feeder row in kiosk (sheet) | 125A | 80A | 3 | 8-probe |  |  | Outstanding |  |  |  | MS 05 - Coral!Q37
MS 05 | K 2,12 | Metering kiosk | K 2,11 | 80A | Inferred from sheet layout | 125A | 60A | 6 | 8-probe |  |  | Outstanding |  |  |  | MS 05 - Coral!Q44
MS 05 | K 2,13 | Metering kiosk | K 2,12 | 60A | Inferred from sheet layout | 60A | NA | 7 | 8-probe |  |  | Outstanding |  |  |  | MS 05 - Coral!Q54
MS 05 | K 2,3 – Block B | Metering kiosk | ? |  | Unconfirmed – not referenced in sheet | 200A | NA | 2 | 8-probe |  |  | Outstanding | K 2.3 | -29.4741 | 31.249 | MS 05 - Coral!V19
MS 05 | K 2,4 – Block A | Metering kiosk | K 2,3 – Block B | 80A · 35mm | Feeder row in kiosk (sheet) | ??A | ??A | 1 | Standalone |  |  | Outstanding | K 2.4 | -29.4739 | 31.2494 | MS 05 - Coral!V26
MS 05 | K 2,21 | Metering kiosk | ? |  | Unconfirmed – not referenced in sheet | 800A | 450A | 3 | 8-probe |  |  | Outstanding | K 2.21 | -29.4736 | 31.2483 | MS 05 - Coral!AF16
MS 05 | K 2,2 | Metering kiosk | K 2,1 | 250A · 2 x 120mm | Feeder row in kiosk (sheet) | 500A | 350A | 4 | 8-probe |  |  | Outstanding | K 2.2 | -29.4735 | 31.2491 | MS 05 - Coral!AF24
MS 05 | K 2,1 | Metering kiosk | ? |  | Unconfirmed – not referenced in sheet | 350A | NA | 4 | 8-probe |  |  | Outstanding | K 2.1 | -29.4734 | 31.2495 | MS 05 - Coral!AF33
MS 06 | MS LV board | MS LV board (direct supplies) | [5 empty] | 1 | Standalone |  |  | Deferred | MS 06 | -29.4795 | 31.2507 | MS 06 row 8–10
MS 06 | K 4,3 | Metering kiosk | MS LV board | 60A | MS LV board (sheet) | 63A | NA | 4 | 8-probe |  | Order 1 | Ordered | K 4.3 | -29.4793 | 31.2511 | MS 06!G13
MS 06 | LV K4,1 | LV distribution kiosk | MS LV board | 125A | MS LV board (sheet) | 125A | ???A | 0 |  |  |  | No supplies | K 4.1 | -29.4795 | 31.2508 | MS 06!L13
MS 06 | HL – 1350 Marula (via LV K4,1) | Metering kiosk | LV K4,1 |  | Kiosk name (sheet) | 100A | NA | 13 | 16-probe | 2cf7f12052601205 | Order 1 | Partly installed | 1350 Marula - DB Room | -29.4796 | 31.2509 | MS 06!L18
MS 06 | LV K5,1 | LV distribution kiosk | MS LV board | 125A | MS LV board (sheet) | 100A | ???A | 0 |  |  |  | No supplies | K 5.1 | -29.4787 | 31.2514 | MS 06!Q13
MS 06 | HL – 1356 Highline (via LV K5,1) | Metering kiosk | LV K5,1 |  | Kiosk name (sheet) | 100A | NA | 13 | 16-probe | 2cf7f1205260267a |  | Installed | 1356 HL - Meter Kiosk | -29.4786 | 31.2517 | MS 06!Q18
MS 06 | K 4,4 | Metering kiosk | MS LV board | 125A | MS LV board (sheet) | 125A | ???A | 4 | 8-probe |  | Order 1 | Ordered | K 4.4 | -29.4794 | 31.2509 | MS 06!V13
MS 06 | K 4,6 | Metering kiosk | K 4,4 |  | Inferred from sheet layout | 100A | ???A | 4 | 8-probe |  | Order 1 | Ordered | K 4.6 | -29.479 | 31.2513 | MS 06!V21
MS 06 | K 4,7 | Metering kiosk | K 4,6 |  | Inferred from sheet layout | 63A | NA | 4 | 8-probe |  | Order 1 | Ordered | K 4.7 | -29.4783 | 31.2518 | MS 06!V29
MS 06 | 498 LV Monyana | LV distribution kiosk | MS LV board | 150A | MS LV board (sheet) | 150A | ???A | 0 |  |  |  | No supplies | 498 Monyana - LV Kiosk | -29.4803 | 31.2508 | MS 06!AA13
MS 06 | 498 Monyana K 1,1 | Metering kiosk | 498 LV Monyana |  | Inferred from sheet layout | 200A | ???A | 3 | 8-probe |  | Order 1 | Ordered |  |  |  | MS 06!AA16
MS 06 | 498 Monyana K 1,2 | Metering kiosk | 498 Monyana K 1,1 |  | Inferred from sheet layout | 63A | ???A | 4 | 8-probe |  | Order 1 | Ordered |  |  |  | MS 06!AA23
MS 06 | 498 Monyana K 1,3 | Metering kiosk | 498 Monyana K 1,2 |  | Inferred from sheet layout | 100A | ???A | 8 | 8-probe |  | Order 1 | Ordered |  |  |  | MS 06!AA31
MS 06 | 498 Monyana K 1,4 | Metering kiosk | 498 Monyana K 1,3 |  | Inferred from sheet layout | 80A | ???A | 2 | 8-probe |  | Order 1 | Ordered |  |  |  | MS 06!AA43
MS 06 | 498 Monyana K 1,5 | Metering kiosk | 498 Monyana K 1,4 |  | Inferred from sheet layout | 50A | ???A | 3 | 8-probe |  | Order 1 | Ordered |  |  |  | MS 06!AA49
MS 06 | 498 Monyana Garage Kiosk | Metering kiosk | 498 Monyana K 1,5 |  | Inferred from sheet layout | 20A | NA | 7 | 8-probe |  | Order 1 | Ordered |  |  |  | MS 06!AA56
MS 07 | MS LV board | MS LV board (direct supplies) | [5 empty] | 1 | Standalone |  |  | Deferred | MS 07 | -29.4799 | 31.2525 | MS 07 row 8–10
MS 07 | Ptn 501 N/S LV Kiosk | LV distribution kiosk | MS LV board | 200A | MS LV board (sheet) | 200A | ???A | 0 |  |  |  | No supplies | Ptn 501 N/S - LV Kiosk | -29.4803 | 31.2511 | MS 07!G13
MS 07 | K 1,1 | Metering kiosk | Ptn 501 N/S LV Kiosk | 160A | Feeder row in kiosk (sheet) | 100A | ???A | 5 | 8-probe |  | Order 1 | Ordered |  |  |  | MS 07!G19
MS 07 | K 1,2 | Metering kiosk | K 1,1 |  | Inferred from sheet layout | 100A | ???A | 5 | 8-probe |  | Order 1 | Ordered |  |  |  | MS 07!G28
MS 07 | K 2,1 | Metering kiosk | Ptn 501 N/S LV Kiosk | 160A | Feeder row in kiosk (sheet) | 100A | ???A | 5 | 8-probe |  | Order 1 | Ordered |  |  |  | MS 07!G37
MS 07 | K 2,2 | Metering kiosk | K 2,1 |  | Inferred from sheet layout | 100A | NA | 5 | 8-probe |  | Order 1 | Ordered |  |  |  | MS 07!G46
MS 07 | Rem 501 V/V K1 | Metering kiosk | MS LV board | 300A | MS LV board (sheet) | 400A | ???A | 10 | 16-probe |  | Order 1 | Ordered | Rem 501 V/V - K1 | -29.4785 | 31.2527 | MS 07!L13
MS 07 | Rem 501 V/V K2 | Metering kiosk | Rem 501 V/V K1 |  | Inferred from sheet layout | 250A | ???A | 8 | 8-probe |  | Order 1 | Ordered | Rem 501 V/V - K2 | -29.4789 | 31.2525 | MS 07!L27
MS 07 | Rem 501 V/V K3 | Metering kiosk | Rem 501 V/V K2 |  | Inferred from sheet layout | 160A | NA | 8 | 8-probe | 2cf7f120526045cf |  | Installed | Rem 501 V/V - K3 | -29.4792 | 31.2524 | MS 07!L39
MS 07 | Club House / Restaurant | Metering kiosk | MS LV board | 200A | MS LV board (sheet) | 150A | ???A | 3 | 8-probe |  | Order 1 | Ordered | ZLM C/H - Main DB | -29.4801 | 31.2527 | MS 07!Q13
MS 08 | KA - LV Kiosk | LV distribution kiosk | MS LV board | 200A | MS LV board (sheet) | 200A | ???A | 0 |  |  |  | No supplies | Reserve - K KA LV Kiosk | -29.4782 | 31.252 | MS 08!B13
MS 08 | 503 Reserve KO | Metering kiosk | KA - LV Kiosk | 200A | Feeder row in kiosk (sheet) | 200A | ???A | 5 | 8-probe |  |  | Outstanding | Reserve - K KO | -29.478 | 31.2529 | MS 08!B19
MS 08 | 503 Reserve KP | Metering kiosk | 503 Reserve KO |  | Inferred from sheet layout | 150A | ???A | 5 | 8-probe |  |  | Outstanding | Reserve - K KP | -29.4777 | 31.253 | MS 08!B28
MS 08 | 503 Reserve KQ | Metering kiosk | 503 Reserve KP |  | Inferred from sheet layout | 150A | NA | 5 | 8-probe |  |  | Outstanding |  |  |  | MS 08!B37
MS 08 | 503 Reserve K503 | Metering kiosk | MS LV board | 200A (shared with KA) | MS LV board (sheet) | 100A | ???A | 3 | 8-probe |  |  | Outstanding | Reserve - K503 | -29.4783 | 31.2528 | MS 08!G13
MS 09 | MS LV board | MS LV board (direct supplies) | [5 empty] | 3 | 8-probe |  |  | Outstanding | MS 09 | -29.4773 | 31.2556 | MS 09 row 8–10
MS 09 | K 9,4 | Metering kiosk | MS LV board | 80A | MS LV board (sheet) | 100A | ???A | 4 | 8-probe |  |  | Outstanding | K 9.4 | -29.478 | 31.2558 | MS 09!Q13
MS 09 | K 9,5 | Metering kiosk | K 9,4 |  | Inferred from sheet layout | 63A | NA | 4 | 8-probe |  |  | Outstanding | K 9.5 | -29.4789 | 31.2562 | MS 09!Q21
MS 09 | K 9,3 | Metering kiosk | MS LV board | 80A | MS LV board (sheet) | 100A | ???A | 5 | 8-probe |  |  | Outstanding | K 9.3 | -29.4767 | 31.2555 | MS 09!V13
MS 09 | K 9,2 | Metering kiosk | K 9,3 |  | Inferred from sheet layout | 100A | ???A | 5 | 8-probe |  |  | Outstanding | K 9.2 | -29.4758 | 31.2563 | MS 09!V22
MS 09 | K 9,1 | Metering kiosk | K 9,2 |  | Inferred from sheet layout | 63A | NA | 4 | 8-probe |  |  | Outstanding | K 9.1 | -29.475 | 31.2565 | MS 09!V31
MS 09 | K 9,9 | Metering kiosk | MS LV board | 150A | MS LV board (sheet) | 160A | ???A | 4 | 8-probe |  |  | Outstanding | K 9.9 | -29.4775 | 31.2553 | MS 09!AA13
MS 09 | K 9,8 | Metering kiosk | K 9,9 |  | Inferred from sheet layout | 250A | ???A | 4 | 8-probe |  |  | Outstanding | K 9.8 | -29.4778 | 31.2553 | MS 09!AA21
MS 09 | K 9,7 | Metering kiosk | K 9,8 |  | Inferred from sheet layout | 100A | ???A | 4 | 8-probe |  |  | Outstanding | K 9.7 | -29.4783 | 31.2554 | MS 09!AA29
MS 09 | K 9,6 | Metering kiosk | K 9,7 |  | Inferred from sheet layout | 63A | NA | 5 | 8-probe |  |  | Outstanding | K 9.6 | -29.4785 | 31.2554 | MS 09!AA37
MS 10 | MS LV board | MS LV board (direct supplies) | [5 empty] | 2 | 8-probe |  |  | Outstanding | MS 10 | -29.4739 | 31.2559 | MS 10 row 8–10
MS 10 | K 10,1 | Metering kiosk | MS LV board | 80A | MS LV board (sheet) | 100A | ???A | 4 | 8-probe |  |  | Outstanding | K 10.1 | -29.4739 | 31.2558 | MS 10!L13
MS 10 | K 10,8 | Metering kiosk | K 10,1 |  | Inferred from sheet layout | 63A | NA | 5 | 8-probe |  |  | Outstanding | K 10.8 | -29.4727 | 31.256 | MS 10!L21
MS 10 | K 10,2 | Metering kiosk | MS LV board | 100A | MS LV board (sheet) | 100A | ???A | 5 | 8-probe |  |  | Outstanding | K 10.2 | -29.4744 | 31.2551 | MS 10!Q13
MS 10 | K 10,3 | Metering kiosk | K 10,2 |  | Inferred from sheet layout | 80A | ???A | 6 | 8-probe |  |  | Outstanding | K 10.3 | -29.4748 | 31.2547 | MS 10!Q22
MS 10 | K 10,4 | Metering kiosk | K 10,3 |  | Inferred from sheet layout | 63A | NA | 4 | 8-probe |  |  | Outstanding | K 10.4 | -29.4752 | 31.2544 | MS 10!Q32
MS 10 | K 10,7 | Metering kiosk | MS LV board | 100A | MS LV board (sheet) | 100A | ???A | 4 | 8-probe |  |  | Outstanding | K 10.7 | -29.4736 | 31.255 | MS 10!V13
MS 10 | K 10,6 | Metering kiosk | K 10,7 |  | Inferred from sheet layout | 63A | ???A | 5 | 8-probe |  |  | Outstanding | K 10.6 | -29.474 | 31.2547 | MS 10!V21
MS 10 | K 10,5 | Metering kiosk | K 10,6 |  | Inferred from sheet layout | 63A | NA | 5 | 8-probe |  |  | Outstanding | K 10.5 | -29.4747 | 31.2542 | MS 10!V30
MS 10 | K 10,9 | Metering kiosk | MS LV board | 100A | MS LV board (sheet) | 100A | ???A | 5 | 8-probe |  |  | Outstanding | K 10.9 | -29.4752 | 31.2557 | MS 10!AA13
MS 10 | K 10,10 | Metering kiosk | K 10,9 |  | Inferred from sheet layout | 63A | NA | 5 | 8-probe |  |  | Outstanding | K 10.10 | -29.4762 | 31.2549 | MS 10!AA22
MS 11 | MS LV board | MS LV board (direct supplies) | [5 empty] | 1 | Standalone |  |  | Outstanding | MS 11 | -29.4756 | 31.2578 | MS 11 row 8–10
MS 11 | K 11,4 | Metering kiosk | MS LV board | 80A | MS LV board (sheet) | 100A | ???A | 5 | 8-probe |  |  | Outstanding | K 11.4 | -29.4748 | 31.2579 | MS 11!G13
MS 11 | K 11,3 | Metering kiosk | K 11,4 |  | Inferred from sheet layout | 63A | NA | 5 | 8-probe |  |  | Outstanding | K 11.3 | -29.4744 | 31.258 | MS 11!G22
MS 11 | K 11,5 | Metering kiosk | MS LV board | 80A | MS LV board (sheet) | 100A | ???A | 6 | 8-probe |  |  | Outstanding | K 11.5 | -29.4758 | 31.2576 | MS 11!L13
MS 11 | K 11,6 | Metering kiosk | K 11,5 |  | Inferred from sheet layout | 100A | ???A | 5 | 8-probe |  |  | Outstanding | K 11.6 | -29.4762 | 31.2573 | MS 11!L23
MS 11 | K 11,7 | Metering kiosk | K 11,6 |  | Inferred from sheet layout | 63A | NA | 5 | 8-probe |  |  | Outstanding | K 11.7 | -29.4764 | 31.2571 | MS 11!L32
MS 11 | K 11,2 | Metering kiosk | MS LV board | 100A | MS LV board (sheet) | 150A | ???A | 5 | 8-probe |  |  | Outstanding | K 11.2 | -29.4741 | 31.2573 | MS 11!Q13
MS 11 | K 11,1 | Metering kiosk | K 11,2 |  | Inferred from sheet layout | 63A | NA | 6 | 8-probe |  |  | Outstanding | K 11.1 | -29.474 | 31.2567 | MS 11!Q22
MS 11 | K 11,8 | Metering kiosk | MS LV board | 150A | MS LV board (sheet) | 160A | ???A | 5 | 8-probe |  |  | Outstanding | K 11.8 | -29.4772 | 31.2568 | MS 11!V13
MS 11 | K 11,9 | Metering kiosk | K 11,8 |  | Inferred from sheet layout | 100A | ???A | 4 | 8-probe |  |  | Outstanding | K 11.9 | -29.4775 | 31.2569 | MS 11!V22
MS 11 | K 11,10 | Metering kiosk | K 11,9 |  | Inferred from sheet layout | 63A | NA | 5 | 8-probe |  |  | Outstanding | K 11.10 | -29.4779 | 31.2571 | MS 11!V30
MS 12 | MS LV board | MS LV board (direct supplies) | [5 empty] | 1 | Standalone |  |  | Outstanding | MS 12 | -29.4746 | 31.2589 | MS 12 row 8–10
MS 12 | K 12,5 | Metering kiosk | MS LV board | 100A | MS LV board (sheet) | 100A | ???A | 4 | 8-probe |  |  | Outstanding | K 12.5 | -29.4759 | 31.2596 | MS 12!G13
MS 12 | K 12,6 | Metering kiosk | K 12,5 |  | Inferred from sheet layout | 63A | ???A | 4 | 8-probe |  |  | Outstanding | K 12.6 | -29.4765 | 31.2602 | MS 12!G21
MS 12 | K 12,7 | Metering kiosk | K 12,6 |  | Inferred from sheet layout | 63A | NA | 4 | 8-probe |  |  | Outstanding | K 12.7 | -29.477 | 31.2608 | MS 12!G29
MS 12 | K 12,11 | Metering kiosk | MS LV board | 100A | MS LV board (sheet) | 100A | ???A | 4 | 8-probe |  |  | Outstanding | K 12.11 | -29.4755 | 31.2605 | MS 12!L13
MS 12 | K 12,12 | Metering kiosk | K 12,11 |  | Inferred from sheet layout | 63A | NA | 4 | 8-probe |  |  | Outstanding | K 12.12 | -29.4758 | 31.2609 | MS 12!L21
MS 12 | K 12,1 | Metering kiosk | MS LV board | 150A | MS LV board (sheet) | 100A | ???A | 4 | 8-probe |  |  | Outstanding | K 12.1 | -29.4745 | 31.2587 | MS 12!Q13
MS 12 | K 12,2 | Metering kiosk | K 12,1 |  | Inferred from sheet layout | 160A | ???A | 4 | 8-probe |  |  | Outstanding | K 12.2 | -29.4747 | 31.259 | MS 12!Q21
MS 12 | K 12,3 | Metering kiosk | K 12,2 |  | Inferred from sheet layout | 100A | ???A | 4 | 8-probe |  |  | Outstanding | K 12.3 | -29.4752 | 31.259 | MS 12!Q29
MS 12 | K 12,4 | Metering kiosk | K 12,3 |  | Inferred from sheet layout | 63A | NA | 4 | 8-probe |  |  | Outstanding | K 12.4 | -29.4761 | 31.2589 | MS 12!Q37
MS 12 | K 12,8 | Metering kiosk | MS LV board | 150A | MS LV board (sheet) | 160A | ???A | 4 | 8-probe |  |  | Outstanding | K 12.8 | -29.475 | 31.2595 | MS 12!V13
MS 12 | K 12,9 | Metering kiosk | K 12,8 |  | Inferred from sheet layout | 100A | ???A | 4 | 8-probe |  |  | Outstanding | K 12.9 | -29.4752 | 31.26 | MS 12!V21
MS 12 | K 12,10 | Metering kiosk | K 12,9 |  | Inferred from sheet layout | 63A | NA | 4 | 8-probe |  |  | Outstanding | K 12.10 | -29.4748 | 31.2603 | MS 12!V29
MS 13 | MS LV board | MS LV board (direct supplies) | [5 empty] | 1 | Standalone |  |  | Outstanding | MS 13 | -29.4732 | 31.2578 | MS 13 row 8–10
MS 13 | K 13,7 | Metering kiosk | MS LV board | 100A | MS LV board (sheet) | 125A | ???A | 4 | 8-probe |  |  | Outstanding | K 13.7 | -29.4732 | 31.2578 | MS 13!G13
MS 13 | K 13,6 | Metering kiosk | K 13,7 |  | Inferred from sheet layout | 125A | ???A | 5 | 8-probe |  |  | Outstanding | K 13.6 | -29.4728 | 31.2577 | MS 13!G21
MS 13 | K 13,5 | Metering kiosk | K 13,6 |  | Inferred from sheet layout | 125A | ???A | 6 | 8-probe |  |  | Outstanding | K 13.5 | -29.4722 | 31.2574 | MS 13!G30
MS 13 | K 13,11 | Metering kiosk | K 13,5 |  | Inferred from sheet layout | 125A | NA | 6 | 8-probe |  |  | Outstanding | K 13.11 | -29.4729 | 31.2582 | MS 13!G40
MS 13 | K 13,8 | Metering kiosk | MS LV board | 100A | MS LV board (sheet) | 125A | ???A | 4 | 8-probe |  |  | Outstanding | K 13.8 | -29.4734 | 31.2585 | MS 13!L13
MS 13 | K 13,9 | Metering kiosk | K 13,8 |  | Inferred from sheet layout | 125A | ???A | 4 | 8-probe |  |  | Outstanding | K 13.9 | -29.4736 | 31.2591 | MS 13!L21
MS 13 | K 13,10 | Metering kiosk | K 13,9 |  | Inferred from sheet layout | 125A | NA | 6 | 8-probe |  |  | Outstanding | K 13.10 | -29.474 | 31.2596 | MS 13!L29
MS 13 | K 13,4 | Metering kiosk | MS LV board | 100A | MS LV board (sheet) | 250A | ???A | 5 | 8-probe |  |  | Outstanding | K 13.4 | -29.4716 | 31.2568 | MS 13!Q13
MS 13 | K 13,3 | Metering kiosk | K 13,4 |  | Inferred from sheet layout | 125A | ???A | 4 | 8-probe |  |  | Outstanding | K 13.3 | -29.4713 | 31.2562 | MS 13!Q22
MS 13 | K 13,2 | Metering kiosk | K 13,3 |  | Inferred from sheet layout | 125A | ???A | 4 | 8-probe |  |  | Outstanding | K 13.2 | -29.4711 | 31.2556 | MS 13!Q30
MS 13 | K 13,1 | Metering kiosk | K 13,2 |  | Inferred from sheet layout | 125A | NA | 5 | 8-probe |  |  | Outstanding | K 13.1 | -29.4711 | 31.255 | MS 13!Q38
MS 14 | MS LV board | MS LV board (direct supplies) | [5 empty] | 1 | Standalone |  |  | Outstanding | MS 14 | -29.472 | 31.2524 | MS 14 row 8–10
MS 14 | K 14,9 A | Metering kiosk | K 14,9 | 80A | Feeder row in kiosk (sheet) | 100A (? *4) |  | 5 | 8-probe |  |  | Outstanding |  |  |  | MS 14!G17
MS 14 | K 14,9 B | Metering kiosk | K 14,9 | 100A | Feeder row in kiosk (sheet) | 100A (? *4) |  | 4 | 8-probe |  |  | Outstanding |  |  |  | MS 14!G26
MS 14 | K 14,10 A | Metering kiosk | K 14,10 | 80A | Feeder row in kiosk (sheet) | 100A (? *4) |  | 4 | 8-probe |  |  | Outstanding |  |  |  | MS 14!G35
MS 14 | K 14,9 | Metering kiosk | MS LV board | 200A | MS LV board (sheet) | 250A (? *4) |  | 6 | 8-probe |  |  | Outstanding | K 14.9 | -29.4717 | 31.2533 | MS 14!L13
MS 14 | K 14,10 | Metering kiosk | K 14,9 |  | Inferred from sheet layout | 125A (? *4) |  | 5 | 8-probe |  |  | Outstanding | K 14.10 | -29.4715 | 31.2539 | MS 14!L25
MS 14 | K 14,11 | Metering kiosk | K 14,10 |  | Inferred from sheet layout | 125A (? *4) |  | 4 | 8-probe |  |  | Outstanding | K 14.11 | -29.4713 | 31.2544 | MS 14!L35
MS 14 | K 14,5 | Metering kiosk | MS LV board | 100A | MS LV board (sheet) | 125A (? *4) |  | 4 | 8-probe |  |  | Outstanding | K 14.5 | -29.4723 | 31.2526 | MS 14!Q13
MS 14 | K 14,4 | Metering kiosk | K 14,5 |  | Inferred from sheet layout | 125A (? *4) |  | 6 | 8-probe |  |  | Outstanding | K 14.4 | -29.4725 | 31.2537 | MS 14!Q21
MS 14 | K 14,3 | Metering kiosk | K 14,4 |  | Inferred from sheet layout | 125A (? *4) |  | 4 | 8-probe |  |  | Outstanding | K 14.3 | -29.4724 | 31.2541 | MS 14!Q31
MS 14 | K 14,2 | Metering kiosk | MS LV board | 150A | MS LV board (sheet) | 125A (? *4) |  | 5 | 8-probe |  |  | Outstanding | K 14.2 | -29.4721 | 31.2549 | MS 14!V13
MS 14 | K 14,1 | Metering kiosk | K 14,2 |  | Inferred from sheet layout | 125A (? *4) |  | 5 | 8-probe |  |  | Outstanding | K 14.1 | -29.4726 | 31.2559 | MS 14!V22

## Minisubs
Minisub | Sheet Name | Manufacturer | Rating | Manufacture Date | Bulk Meter Serial | Bulk AMR Device | Bulk Last Comms | Bulk on AMR | LV Board Outgoing Circuits | Latitude | Longitude
MS 01 | MS 01 | PowerTech | 500 kVA (800A) | 10/2017 | 63237040 | 2cf7f1204330c5b3 | 10/5/2026, 11:35 AM | Yes | 60A - Double Connection → Main Gatehouse -- Contractors Gate; 60A → Streetlights; 200A → Nothing Connected; 200A → Nothing Connected; 250A → 505 - Aura Bulk | -29.4825 | 31.2501
MS 02 | MS 02 | PowerTech | 500 kVA (800A) | 10/2017 | 63237017 | 2cf7f1205020c1ab | 10/5/2026, 12:16 PM | Yes | 60A → Streetlights; 200A → Kiosk 2,1; 200A → 511 - Husk Bulk; 250A → 513 - Azure LV Kiosk; 200A → 512 | -29.4821 | 31.2522
MS 03 | MS 03 | SGB-Smit Power Malta | 315 kVA (450A) | 08/2019 | 63237024 | 2cf7f12063102abc | 10/5/2026, 12:02 PM | Yes | 32A → Streetlights Kiosk; 60A → K 3,1; 80A → 1336 - Savili; 100A → K 3,2; 100A → K 3,4; 125A → K 2,3; 400A → 1707 - Sea La Vie | -29.4811 | 31.2491
MS 04 | MS 04 - Coral | Electronic Assemblies (PTY) Ltd. | 500 kVA (700A) | ??? | 90915109 |  |  | No | 120A → K 1,1; 120A → K 1,4; 250A → K 1,10 | -29.474 | 31.2506
MS 05 | MS 05 - Coral | Electronic Assemblies (PTY) Ltd. | 800 kVA (1200A) | 2024 | 91074243 |  |  | No | 60A → Streetlights 2,1; 200A → K 2,5; 250A → K 2,9; 200A → K 2,10; 1000A → Generator | -29.4736 | 31.248
MS 06 | MS 06 | PowerTech | 315 kVA (450A) | 06/2018 | 63237041 | 2cf7f1205020c8fd | 10/5/2026, 12:09 PM | Yes | 32A → Streetlights; 60A → K 4,3; 125A → K 4,1 - 1350 Marula; 125A → K 5,1 - 1356 Highline; 125A → K 4,4; 150A → 498 - LV Monyana | -29.4795 | 31.2507
MS 07 | MS 07 | PowerTech | 315 kVA (500A) | 06/2016 | 83014676 | 2cf7f1204330c524 | 10/5/2026, 11:54 AM | Yes | 63A → Streetlights; 200A → Ptn 501 - North Shore; 300A → Rem 501 - Valley Views; 200A → Club House & Restaurant Ref. Meter | -29.4799 | 31.2525
MS 08 | MS 08 | SGB-Smit Power Malta | 315 kVA (450A) | 08/2020 | 83014670 | 2cf7f1205020c40a | 10/5/2026, 11:42 AM | Yes | 200A → 503 - Reserve K.KA LV Kiosk & 503; 100A → Nothing Connected; 32A → Nothing Connected | -29.4782 | 31.252
MS 09 | MS 09 | SGB-Smit Power Malta | 315 kVA (450A) | 05/2019 | 82929637 | 2cf7f1204330c576 | 10/5/2026, 11:50 AM | Yes | 100A → Sewer Pump Station; 100A → Pump Station; 60A → Streetlights; 80A → K 9,4; 80A → K 9,3; 150A → K 9,9 | -29.4773 | 31.2556
MS 10 | MS 10 | SGB-Smit Power Malta | 315 kVA (450A) | 05/2019 | 63237027 | 2cf7f12050200872 | 10/5/2026, 12:26 PM | Yes | 200A → Sewer Pump Station; 63A → Streetlights Kiosk; 80A → K 10,1; 100A → K 10,2; 100A → K 10,7; 100A → K 10,9 | -29.4739 | 31.2559
MS 11 | MS 11 | SGB-Smit Power Malta | 315 kVA (450A) | 2019 | 63237016 | 2cf7f1205020bc2b | 10/5/2026, 12:00 PM | Yes | 63A → Streetlights Kiosk; 80A → K 11,4; 80A → K 11,5; 100A → K 11,2; 150A → K 11,8 | -29.4756 | 31.2578
MS 12 | MS 12 | SGB-Smit Power Malta | 315 kVA (450A) | 05-2019 | 82929673 | 2cf7f1205020c201 | 10/5/2026, 11:38 AM | Yes | 60A → Streetlights Kiosk; 100A → K 12,5; 100A → K 12,11; 150A → K 12,1; 150A → K 12,8 | -29.4746 | 31.2589
MS 13 | MS 13 | Electronic Assemblies (PTY) Ltd. | 315 kVA (450A) | 2021 | 83013672 | 2cf7f1205100c4e5 | 10/5/2026, 11:53 AM | Yes | 60A → Streetlights; 100A → K 13,7; 100A → K 13,8; 100A → K 13,4 | -29.4732 | 31.2578
MS 14 | MS 14 | Electronic Assemblies (PTY) Ltd. | 315 kVA (450A) | 2021 | 83013703 | 2cf7f1205020bab8 | 10/5/2026, 11:39 AM | Yes | 63A → NA; 63A → Streetlights; 200A → K 14,9; 100A → K 14,5; 150A → K 14,2 | -29.472 | 31.2524

## AMR Devices
Device (SNR) | Minisub | Location | Channels Used | Highest Port | Device Size | Supplies
2cf7f1204330c5b3 | MS 01 | MS bulk meter | 1 |  | Bulk meter device | 63237040
2cf7f120526010ac | MS 02 | 511 Husk Meter Panel 1 | 10 | 10 | 16-probe (assumed) | 511-01, 511-02, 511-03, 511-04, 511-05, 511-06, 511-07, 511-08, 511-09, 511-10
2cf7f120526050b8 | MS 02 | 511 Husk Meter Panel 2 | 14 | 14 | 16-probe (assumed) | 511-11, 511-12, 511-13, 511-14, 511-15, 511-16, 511-17, 511-18, 511-19, 511-20, 511-21, 511-22, 511-23, 511-24
2cf7f1205020c1ab | MS 02 | MS bulk meter | 1 |  | Bulk meter device | 63237017
2cf7f12063102abc | MS 03 | MS bulk meter | 1 |  | Bulk meter device | 63237024
2cf7f12052601205 | MS 06 | HL – 1350 Marula (via LV K4,1) | 10 | 10 | 16-probe (assumed) | 1350-02, 1350-01, 1350-03, 1350-04, 1350-05, 1350-06, 1350-07, 1350-08, 1350-09, 1350-12
2cf7f1205260267a | MS 06 | HL – 1356 Highline (via LV K5,1) | 13 | 13 | 16-probe (assumed) | 1356-01, 1356-02, 1356-03, 1356-04, 1356-05, 1356-06, 1356-07, 1356-08, 1356-09, 1356-10, 1356-11, 1356-12, Communal
2cf7f1205020c8fd | MS 06 | MS bulk meter | 1 |  | Bulk meter device | 63237041
2cf7f1204330c524 | MS 07 | MS bulk meter | 1 |  | Bulk meter device | 83014676
2cf7f120526045cf | MS 07 | Rem 501 V/V K3 | 8 | 8 | 8-probe | REM 501/22, REM 501/19, REM 501/20, REM 501/26, REM 501/24, REM 501/23, REM 501/25, REM 501/21
2cf7f1205020c40a | MS 08 | MS bulk meter | 1 |  | Bulk meter device | 83014670
2cf7f1204330c576 | MS 09 | MS bulk meter | 1 |  | Bulk meter device | 82929637
2cf7f12050200872 | MS 10 | MS bulk meter | 1 |  | Bulk meter device | 63237027
2cf7f1205020bc2b | MS 11 | MS bulk meter | 1 |  | Bulk meter device | 63237016
2cf7f1205020c201 | MS 12 | MS bulk meter | 1 |  | Bulk meter device | 82929673
2cf7f1205100c4e5 | MS 13 | MS bulk meter | 1 |  | Bulk meter device | 83013672
2cf7f1205020bab8 | MS 14 | MS bulk meter | 1 |  | Bulk meter device | 83013703

## Orders
Order | Date Placed | Item | Quantity | Allocated To | Notes
Order 1 | 2026-10 | 16-probe unit | 1 | MS 07 Rem 501 V/V K1 | MS 07 + MS 06
Order 1 | 2026-10 | 8-probe unit | 19 | 16 allocated (MS 07: 6, MS 06: 10), 3 spare | Spare can cover 1350 Marula if existing device is full
Order 1 | 2026-10 | Probe | 100 | 87 allocated, 13 spare | Incl. 3 for 1350 Marula on existing device

## Data Issues
Severity | Type | Minisub | Issue
High | Missing units | MS 02 | Sheet header says 50 built stands, but only 26 are listed. 511 Husk (bulk meter 83013636, "Meter panel 1 & 2" in KMZ) has no unit rows – roughly 24 supplies not counted.
High | Missing units | MS 05 – Coral | Header says 63 built; 38 stands listed. K 2,3 (DB-B-01, Block B) and K 2,4 (DB-A-01, Block A) are bulk feeds to buildings whose flats are not listed – counted as 1 supply each.
High | Missing units | MS 08 | Header says 45 vacant stands, but only 18 supplies are listed in kiosks K503/KO/KP/KQ. Future 503 Reserve stands have no kiosk allocation yet – not counted.
Medium | Header mismatch | MS 03 | Header counts 17/3/22 (built/constr/vacant) – excludes the 52 x 1707 Sea La Vie flats (+ 8 collection lights) in 1707 K 3,4–3,10, which are included here as requested.
Low | Header mismatch | MS 04 / 06 / 10 / 14 | Listed vs header differ by 1 (e.g. MS 04 built 51 vs 50, MS 10 built 29 vs 28, MS 14 vacant 23 vs 24). Likely header not updated after the last edit.
High | Duplicate | MS 11 / MS 12 | Stand 1213 with meter 87819359 is listed in both MS 11 K 11,3 (G27) and MS 12 K 12,1 (Q16). One is wrong; both counted for now.
Medium | Duplicate | MS 03 | Stand 1315 listed in K 3,3 (Q29) and K 3,5 (V25).
Medium | Duplicate | MS 06 | 498 Monyana garage meters share serials with units: 42576456 (498-04 & 498-1G), 42576489 (498-08B & 498-3G), 42576526 (498-09A & 498-2G).
Medium | Duplicate kiosk label | MS 03 | K 3,4, K 3,5 and K 3,10 each appear twice: once as stand kiosks (col V) and once as 1707 Sea La Vie kiosks (col AF/AP). Also the MS board feeds "K 3,4" and the 1707 LV kiosk feeds "K 3,4". Renamed the 1707 ones "1707 K 3,x" here; KMZ points K 3.4/3.5/3.10 assigned to the stand kiosks.
Info | Interpretation | All | Status taken from cell colour per the legend: green = ON (built), yellow = ON (construction site), orange = OFF (vacant). 13 rows have no colour (MS 02 512 placeholder rows, K 2,3/2,4 block DBs, K 2,11 streetlights, 2 S/L collection supplies).
Info | Interpretation | All | 110 placeholder slots ("???" or "-") counted as planned supplies (one probe each).
Info | Interpretation | MS 02 | 512 Kiosk 3 and Kiosk 6 are marked "Kiosk to be installed" – their blank rows (2 each) are taken as planned slots.
Info | Interpretation | All | 1 probe per supply. 24 three-phase supplies counted as 1 probe each (6 stands: 1704, 1247, 1636, 1634, 1655, 1667; plus 18 common loads mainly in Coral MS 05).
Info | Interpretation | All | Excluded: kiosk-to-kiosk feeders, surge arrestors, MS 05 generator (source), empty LV distribution kiosks (LV K4,1, LV K5,1, Ptn 501 N/S LV, KA LV).
Info | Interpretation | All | Supplies fed straight off a minisub LV board (streetlights, gatehouses, sewer/pump stations) are grouped per minisub: 1 supply = standalone unit, 2+ = one 8-probe unit at the minisub.
Info | Interpretation | MS 01 | "Main Gatehouse -- Contractors Gate" is one 60A double-connection breaker feeding two kiosks with separate meters – counted as 2 supplies.
Info | Interpretation | MS 02 / MS 03 | Collection meters (513 S/L kiosk, 1707 Ex/Lights & CP/Lights) counted as supplies that need a probe.
Info | Scope | All | You mentioned 12 minisubs – both the Excel and KMZ have 14 (MS 01–MS 14, incl. MS 04 & MS 05 Coral). All 14 included.
Low | KMZ vs Excel | MS 01 | "Contractors G/H": KMZ point (MS 01 gatehouse) – Excel lists it as a direct MS supply; drawn at MS 01.
Low | KMZ vs Excel | MS 01 | "Main G/H & Office": KMZ point (MS 01 gatehouse) – Excel lists it as a direct MS supply; drawn at MS 01.
Low | KMZ vs Excel | MS 02 | "511 Husk - Meter panel 1": In KMZ but no unit list in Excel (see 511 Husk above).
Low | KMZ vs Excel | MS 02 | "511 Husk - Meter panel 2": In KMZ but no unit list in Excel (see 511 Husk above).
Medium | KMZ vs Excel | MS 06 | "K 4.5": Kiosk K 4.5 is in KMZ but not in the Excel (MS 06 has K 4,3 / 4,4 / 4,6 / 4,7 only).
Low | KMZ vs Excel | MS 06 | "498 Monyana - LV Kiosk": Used as the map anchor for the 498 Monyana kiosks (K 1,1–1,5 + Garage), which have no own KMZ points.
Medium | KMZ vs Excel | MS 14 | "Seaton G/H": In KMZ but not in Excel. MS 14 has a 63A outgoing breaker labelled "NA" – possibly this gatehouse supply?
Medium | KMZ vs Excel | Several | 53 Excel kiosks have no KMZ point (505 Aura K01–K12; 512 Kiosks 1–6; 513 K 1,1–1,5; 1707 kiosks; Coral K 2,7/2,8/2,11/2,11A/2,12/2,13/2,18; 498 Monyana kiosks; North Shore K 1,1–2,2; 503 KQ; K 14,9 A/B, K 14,10 A). On the map they are grouped as a grey marker at the nearest known point.
Medium | Topology | All | "Fed From" is taken from the sheet where stated (MS LV board circuits, feeder rows inside kiosks). Elsewhere it is inferred from the vertical order of kiosks in the sheet (same column = daisy chain) – check against as-built SLDs. Rows marked "Unconfirmed" could not be placed.
Medium | AMR export | MS 06 | Meter 90007923 is labelled "1350 - 10" on AMR but is 1350-12 in the sheet; 1350-10, 1350-11 and Communal are not on AMR.
Medium | AMR export | MS 06 | Stale comms: 1356-1 (27 Aug), 1350-3 and 1350-6 (22 Sep).
Low | AMR export | MS 02 | 511-16 meter removed (serial shown as 90007892xxx) – AMR channel still registered.
Low | AMR export | MS 04 / MS 05 | Coral minisub bulk meters (90915109, 91074243) are not on AMR.